## ANALIZA OPTIUNI
Sistem de canalizare | CLUSTER BELIN
Water Activity Options |  | Sisteme de alimentare cu apa a comunei Ghercesti
Analysis 1 |  | Option 1 | Option 2 |  |  | Short description of Option 1
Alimentarea cu apa din reteaua de distributie a municipiului Craiova
Investment costs | Euro | 0 | 0
Main works | Euro
Plant and Machinery | Euro
Quantity fo water related to options | m3 |  |  |  |  | Short description of Option 2
Alimentarea cu apa de la sursa subterana proprie Ghercesti
Operating costs
Material Costs | Euro | 0 | 0
Personnel Costs | Euro | 0 | 0
Number | no.
Average salary | Euro/Month | 400 | 400
Related taxes | Euro/Month | 124 | 124
Electricity costs | Euro | 0 | 0
Quantity | KwH/year
Average price | Euro/KwH | 0.11 | 0.11
Maintenance costs | Euro | 0 | 0
Percentage from Main Works | % | 0.5% | 0.5%
Percentage from Plant and Machinery | % | 1.5% | 1.5%
Total operating costs | Euro | 0 | 0 |  |  | Option selected from technical point of view: |  |  |  | Option 1
Analysis 2 |  | Option 1 | Option 2 | Option 3 |  | Short description of Option 1
Investment costs | Euro | 0 | 0 | 0
Main works | Euro | 0 | 0 | 0
Plan and Machinery | Euro | 0 | 0 | 0
Quantity fo water related to options | m3 | 0 | 0 | 0 |  | Short description of Option 2
Operating costs
Material Costs | Euro | 0 | 0 | 0
Personnel Costs | Euro | 0 | 0 | 0
Number | no. | 0 | 0 | 0
Average salary | Euro/Month | 400 | 400 | 400 |  | Short description of Option 3
Related taxes | Euro/Month | 124 | 124 | 124
Electricity costs | Euro | 0 | 0 | 0
Quantity | KwH/year | 0 | 0 | 0
Average price | Euro/KwH | 0.11 | 0.11 | 0.11
Maintenance costs | Euro | 0 | 0 | 0
Percentage from Main Works | % | 0% | 0% | 0%
Percentage from Plan and Machinery | % | 0% | 0% | 0%
Total operating costs | Euro | 0 | 0 | 0 |  | Option selected from technical poin of view: |  |  |  | Option 1
Optiuni pentru sistemul de canalizare |  | AGLOMERAREA BELIN
Analiza 1 |  | Optiunea 1 | Optiunea 2 |  | Scurta descriere a Optiunii 1 | [8 empty] | .
Descarcarea debitelor de apă uzată din Aglomerararea Belin in SEAU noua Belin.
Investment costs | Euro | 1067096.3 | 0
Constructii | Euro | 431700 | 0
Echipamente si instalatii | Euro | 635396.3 | 0
Volum de apa | m3/an | 157364.64 | 157364.64 |  | Scurta descriere a Optiunii 2
Descarcarea debitelor de apă uzată din Aglomerararea Belin in SEAU Sfantu Gheorghe existenta.
Costuri de operare totale | Euro | 80121.9089 | 8057.174
Costuri cu materiale | Euro | 3893.0679 | 3893.0679
Costuri cu personalul | Euro | 38880 | 0
Numar | no. | 3 | 0
Salariul mediu | Euro/luna | 600 | 600
Taxe | Euro/luna | 480 | 480
Costuri cu energia electrica | Euro | 25406.4709 | 4164.1061
Cantitate | KwH/an | 230967.9174 | 37855.5098
Pret | Euro/KwH | 0.11 | 0.11
Costuri de intretinere | Euro | 11689.4445 | 0
Procent din investitie - constructii | % | 0.5% | 0.5%
Procent din investitie - echipamente si instalatii | % | 1.5% | 1.5%
Costuri cu transportul namolului |  | 252.9255 | 0
Cantitate | t/an | 224.8227 | 0
Cost transport | Euro/km | 1 | 1
[6 empty] | Optiunea selectata din punct de vedere economic |  |  |  | Optiunea xxx
Analysis 2 |  | Option 1 | Option 2 | Option 3 |  | Short description of Option 1
Investment costs | Euro | 0 | 0 | 0
Main works | Euro | 0 | 0 | 0
Plan and Machinery | Euro | 0 | 0 | 0
Quantity fo water related to options | m3 | 0 | 0 | 0 |  | Short description of Option 2
Operating costs
Material Costs | Euro | 0 | 0 | 0
Personnel Costs | Euro | 0 | 0 | 0
Number | no. | 0 | 0 | 0
Average salary | Euro/Month | 400 | 400 | 400 |  | Short description of Option 3
Related taxes | Euro/Month | 124 | 124 | 124
Electricity costs | Euro | 0 | 0 | 0
Quantity | KwH/year | 0 | 0 | 0
Average price | Euro/KwH | 0.11 | 0.11 | 0.11
Maintenance costs | Euro | 0 | 0 | 0
Percentage from Main Works | % | 0% | 0% | 0%
Percentage from Plan and Machinery | % | 0% | 0% | 0%
Sludge disposal costs |  | 0 | 0 | 0
Quantity | tDM/a | 0 | 0 | 0
Average costs of disposal | Euro/tDM | 25 | 25 | 25
Total operating costs | Euro | 0 | 0 | 0 |  | Option selected from technical poin of view: |  |  |  | Option 1
Analiza financiara a optiunilor
Water activity
Analysis 1
Option 1 | [12 empty] | Option 2
Year | Investment |  | Operating and maintenance costs | [5 empty] | Financial |  |  |  | Year | Investment |  | Operating and maintenance costs | [6 empty] | Financial
| Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Toal | Total | unit |  |  |  |  | Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Toal | Total |  | unit
|  | Machinery | costs | costs | costs | costs | O&M | Water | cost | [5 empty] | Machinery | costs | costs | costs | costs | O&M | Water |  | cost
[7 empty] | cost | Quantity | per m3 | [10 empty] | cost | Quantity |  | per m3
| Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3 |  |  |  |  | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 |  | EUR/m3
2009 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 2009 | 0 | 0 |  |  |  |  | 0 | 0
2010 | 0 | 0 |  |  |  |  | 0 | 0 |  | 10% |  |  | 2010 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 10%
2011 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30% |  |  | 2011 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 30%
2012 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30% |  |  | 2012 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 30%
2013 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30% |  |  | 2013 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 30%
2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100% | 0
2015 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2015 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2016 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2016 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2017 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2017 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2018 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2018 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2019 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2019 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2020 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2020 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NPV at 4% | 0 | 0 |  |  |  |  | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 4% | 0 | 0 |  |  |  |  | #DIV/0! | 0 |  | #DIV/0!
Analysis 2
Option 1 | [12 empty] | Option 2 | [13 empty] | Option 3
Year | Investment |  | Operating and maintenance costs | [5 empty] | Financial |  |  |  | Year | Investment |  | Operating and maintenance costs | [6 empty] | Financial |  |  |  | Year | Investment |  | Operating and maintenance costs | [5 empty] | Financial
| Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Toal | Total | unit |  |  |  |  | Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Toal | Total |  | unit |  |  |  |  | Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Toal | Total | unit
|  | Machinery | costs | costs | costs | costs | O&M | Water | cost | [5 empty] | Machinery | costs | costs | costs | costs | O&M | Water |  | cost | [5 empty] | Machinery | costs | costs | costs | costs | O&M | Water | cost
[7 empty] | cost | Quantity | per m3 | [10 empty] | cost | Quantity |  | per m3 | [10 empty] | cost | Quantity | per m3
| Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3 |  |  |  |  | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 |  | EUR/m3 |  |  |  |  | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3
2009 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 2009 | 0 | 0 |  |  |  |  | 0 | 0 | [5 empty] | 2009 | 0 | 0 |  |  |  |  | 0 | 0
2010 | 0 | 0 |  |  |  |  | 0 | 0 |  | 10% |  |  | 2010 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 10% |  |  | 2010 | 0 | 0 |  |  |  |  | 0 | 0 |  | 10%
2011 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30% |  |  | 2011 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 30% |  |  | 2011 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30%
2012 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30% |  |  | 2012 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 30% |  |  | 2012 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30%
2013 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30% |  |  | 2013 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 30% |  |  | 2013 | 0 | 0 |  |  |  |  | 0 | 0 |  | 30%
2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100% | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% | 0
2015 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2015 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2015 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2016 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2016 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2016 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2017 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2017 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2017 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2018 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2018 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2018 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2019 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2019 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2019 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2020 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2020 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2020 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  |  | 2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0 | [5 empty] | 2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | 0
Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NPV at 4% | 0 | 0 |  |  |  |  | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 4% | 0 | 0 |  |  |  |  | #DIV/0! | 0 |  | #DIV/0!
Apa uzata
Analiza 1
Optiunea 1 | [13 empty] | Optiunea 2 | [14 empty] | Option 3
An | Investitii |  | Operating and maintenance costs | [6 empty] | Cost |  |  |  | An | Investitii |  | Operating and maintenance costs | [7 empty] | Cost |  |  |  | Year | Investment |  | Operating and maintenance costs | [6 empty] | Financial
| Lucrari civile | Constructii | Costuri cu | Costuri cu | Costuri cu | Costuri cu | Costuri cu | Cost total | Volum | unitar |  |  |  |  | Lucrari civile | Constructii | Costuri cu | Costuri cu | Costuri cu | Costuri cu | Costuri cu | Costuri de | Cost total | Volum | unitar |  |  |  |  | Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Sludge | Toal | Total | unit
|  | Instalatii | materialel | electricitatea | personalul | intretinerea | depozitarea | operare si | apa uzata | pe m3 | [5 empty] | Instalatii | materialel | electricitatea | personalul | intretinerea | depozitarea | operare | operare si | apa uzata | pe m3 | [5 empty] | Machinery | costs | costs | costs | costs | disposal | O&M | wastewater | cost
[7 empty] | namolului | mentenanta | [12 empty] | namolului | SE TG | mentenanta | [12 empty] | costs | cost | Quantity | per m3
| Euro | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3 |  |  |  |  | Euro | Euro | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3 |  |  |  |  | Euro | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3
2018 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 2018 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 2009 | 0 | 0 | [5 empty] | 0 | 0
2019 | 43170 | 63539.63 | [5 empty] | 0 | 0 |  | 10% |  |  | 2019 | 0 | 0 | [6 empty] | 0 | 0 |  | 10% |  |  | 2010 | 0 | 0 | [5 empty] | 0 | 0 |  | 10%
2020 | 129510 | 190618.89 | [5 empty] | 0 | 0 |  | 30% |  |  | 2020 | 0 | 0 | [6 empty] | 0 | 0 |  | 30% |  |  | 2011 | 0 | 0 | [5 empty] | 0 | 0 |  | 30%
2021 | 129510 | 190618.89 | [5 empty] | 0 | 0 |  | 30% |  |  | 2021 | 0 | 0 | [6 empty] | 0 | 0 |  | 30% |  |  | 2012 | 0 | 0 | [5 empty] | 0 | 0 |  | 30%
2022 | 129510 | 190618.89 | [5 empty] | 0 | 0 |  | 30% |  |  | 2022 | 0 | 0 | [6 empty] | 0 | 0 |  | 30% |  |  | 2013 | 0 | 0 | [5 empty] | 0 | 0 |  | 30%
2023 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  | 100% | 0 |  | 2023 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  | 100% | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% | 0
2024 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2024 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2025 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2026 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2027 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2028 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2029 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2030 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2031 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2032 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2033 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2034 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2035 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2035 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2036 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2036 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2037 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2037 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2038 | 0 | 63539.63 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2038 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2039 | 0 | 190618.89 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2039 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2040 | 0 | 190618.89 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2040 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2041 | 0 | 190618.89 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2041 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2042 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2042 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2043 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2043 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2044 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2044 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2045 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2045 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2046 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2046 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2047 | 0 | 0 | 3893.0679 | 25406.4709 | 38880 | 11689.4445 | 252.9255 | 80121.9089 | 157364.64 |  |  |  |  | 2047 | 0 | 0 | 3893.0679 | 4164.1061 | 0 | 0 | 0 | 0 | 8057.174 | 157364.64 |  |  |  |  | 2038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Valoarea reziduala | -161887.5 | -381237.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Valoarea reziduala | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NPV la 4% | 337175.5614 | 722612.6804 | [5 empty] | 1069933.5016 | 2101418.9838 | 1.0135 |  |  |  | NPV la 4% | 0 | 0 | [6 empty] | 107594.0468 | 2101418.9838 | 0.051201 |  |  |  | NPV at 5% | 0 | 0 | [5 empty] | 0 | 0 | #DIV/0!
Analysis 2
Option 1 | [13 empty] | Option 2 | [14 empty] | Option 3
Year | Investment |  | Operating and maintenance costs | [6 empty] | Financial |  |  |  | Year | Investment |  | Operating and maintenance costs | [7 empty] | Financial |  |  |  | Year | Investment |  | Operating and maintenance costs | [6 empty] | Financial
| Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Sludge | Toal | Total | unit |  |  |  |  | Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Sludge |  | Toal | Total | unit |  |  |  |  | Main works | Plant and | Materials | Elecricity | Personnel | Maintenance | Sludge | Toal | Total | unit
|  | Machinery | costs | costs | costs | costs | disposal | O&M | wastewater | cost | [5 empty] | Machinery | costs | costs | costs | costs | disposal |  | O&M | wastewater | cost | [5 empty] | Machinery | costs | costs | costs | costs | disposal | O&M | wastewater | cost
[7 empty] | costs | cost | Quantity | per m3 | [10 empty] | costs |  | cost | Quantity | per m3 | [10 empty] | costs | cost | Quantity | per m3
| Euro | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3 |  |  |  |  | Euro | Euro | Euro | Euro | Euro | Euro | Euro |  | Euro | m3 | EUR/m3 |  |  |  |  | Euro | Euro | Euro | Euro | Euro | Euro | Euro | Euro | m3 | EUR/m3
2015 | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 2015 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 2009 | 0 | 0 | [5 empty] | 0 | 0
2016 | 0 | 0 | [5 empty] | 0 | 0 |  | 10% |  |  | 2016 | 0 | 0 | [6 empty] | 0 | 0 |  | 10% |  |  | 2010 | 0 | 0 | [5 empty] | 0 | 0 |  | 10%
2017 | 0 | 0 | [5 empty] | 0 | 0 |  | 30% |  |  | 2017 | 0 | 0 | [6 empty] | 0 | 0 |  | 30% |  |  | 2011 | 0 | 0 | [5 empty] | 0 | 0 |  | 30%
2018 | 0 | 0 | [5 empty] | 0 | 0 |  | 30% |  |  | 2018 | 0 | 0 | [6 empty] | 0 | 0 |  | 30% |  |  | 2012 | 0 | 0 | [5 empty] | 0 | 0 |  | 30%
2019 | 0 | 0 | [5 empty] | 0 | 0 |  | 30% |  |  | 2019 | 0 | 0 | [6 empty] | 0 | 0 |  | 30% |  |  | 2013 | 0 | 0 | [5 empty] | 0 | 0 |  | 30%
2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 100% | 0 |  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% | 0
2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2015 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2016 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2017 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2018 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2019 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2020 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2021 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2022 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2023 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2024 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2025 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2026 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2027 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2028 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2029 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2030 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2031 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2032 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2039 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2039 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2033 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2040 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2040 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2034 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2041 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2041 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2035 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2042 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2042 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2036 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2037 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0 |  |  |  |  | 2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  |  |  |  | 2038 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | 0
Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | Resid. Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NPV at 0% | 0 | 0 | [5 empty] | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 0% | 0 | 0 | [6 empty] | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 0% | 0 | 0 | [5 empty] | #DIV/0! | 0 | #DIV/0!
NPV at 5% | 0 | 0 | [5 empty] | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 5% | 0 | 0 | [6 empty] | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 5% | 0 | 0 | [5 empty] | #DIV/0! | 0 | #DIV/0!
NPV at 10% | 0 | 0 | [5 empty] | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 10% | 0 | 0 | [6 empty] | #DIV/0! | 0 | #DIV/0! |  |  |  | NPV at 10% | 0 | 0 | [5 empty] | #DIV/0! | 0 | #DIV/0!
Water Activity Options
Analysis 1 | Option 1 | Option 2
NPV at 4% | #DIV/0! | #DIV/0!
Optiuni privind sistemul de canalizare
Analiza 1 | Optiunea 1 | Optiunea 2
DUC | 1.0135 | 0.051201
NPV la 4% | 2129721.7434 | 107594.0468
Descriere optiuni sistem alimentare cu apa
Opţiunea 1
Opţiunea 2
Analysis 2
NPV at 5%

## INVESTITII CANAL
INVESTITII (Euro)
Optiunea 1 (varianta descentralizata)
|  | UM | Cantitate | Lucrari civile | Utilaje si echipamente | TOTAL (euro)
Aglomerarea Belin | Descarcare in SEAU Belin noua
| Retea de canalizare | m
SPAU
buc
Refulari
SEAU
| Statie de epurare noua in Sanzieni - 2.700 l.e. | buc | 1 | 431700 | 635396.3 | 1067096.3
| TOTAL |  |  | 431700 | 635396.3 | 1067096.3
Optiunea 2 (varianta centralizata)
Aglomerarea Belin | Descarcare in SEAU Sfantu Gheorghe existenta
|  | UM | Cantitate | Lucrari civile | Utilaje si echipamente | TOTAL (euro)
Retea de canalizare
|  | m | 0 |  |  | 0
|  | m |  | 0 |  | 0
SPAU
buc
Refulari
| TOTAL |  |  | 0 | 0 | 0

## COND CANAL H=1-6 m
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [29 empty] | 1
Hg = 1 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDEN-TAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 1.06 | 0.8056 | 3.14 | 2.5296 | 0.25833 | 19.55 | 5.0503 | 0.52718 | 2.23 | 1.1756 | 2.12 | 5.67 | 0 | 8.7555 | 0.27842 | 1.4793 | 10.2347 | 9.87 | 408 | 10.2 | 30.3047 | 34.8505 | 73 | 72 | 15 | 107.8505 | 106.8505 | 49.8505
| 200 | 0.2 | 0.8 | 1.1 | 0.88 | 3.14 | 2.7632 | 0.29488 | 19.55 | 5.7649 | 0.55372 | 2.23 | 1.2348 | 2.2 | 5.67 | 0 | 9.7629 | 0.32628 | 1.7335 | 11.4964 | 11.9 | 408 | 10.2 | 33.5964 | 38.6359 | 82 | 81 | 17 | 120.6359 | 119.6359 | 55.6359
| 250 | 0.25 | 0.85 | 1.15 | 0.9775 | 3.14 | 3.0694 | 0.3408 | 19.55 | 6.6626 | 0.58764 | 2.23 | 1.3104 | 2.3 | 5.67 | 0 | 11.0424 | 0.38986 | 2.0713 | 13.1137 | 17 | 408 | 10.2 | 40.3137 | 46.3607 | 82 | 81 | 17 | 128.3607 | 127.3607 | 63.3607
| 300 | 0.315 | 0.915 | 1.215 | 1.1117 | 3.14 | 3.4908 | 0.39995 | 19.55 | 7.8191 | 0.63388 | 2.23 | 1.4136 | 2.43 | 5.67 | 0 | 12.7235 | 0.47785 | 2.5388 | 15.2623 | 24.68 | 408 | 10.2 | 50.1423 | 57.6636 | 91 | 90 | 19 | 148.6636 | 147.6636 | 76.6636
| 355 | 0.355 | 0.955 | 1.255 | 1.1985 | 3.14 | 3.7634 | 0.43555 | 19.55 | 8.5149 | 0.66405 | 2.23 | 1.4808 | 2.51 | 5.67 | 0 | 13.7591 | 0.53448 | 2.8397 | 16.5988 | 31.35 | 408 | 10.2 | 58.1488 | 66.8711 | 91 | 90 | 19 | 157.8711 | 156.8711 | 85.8711
| 400 | 0.4 | 1 | 1.3 | 1.3 | 3.14 | 4.082 | 0.4744 | 19.55 | 9.2745 | 0.7 | 2.23 | 1.561 | 2.6 | 5.67 | 0 | 14.9175 | 0.6 | 3.1878 | 18.1053 | 38.44 | 408 | 10.2 | 66.7453 | 76.7571 | 105 | 103 | 22 | 181.7571 | 179.7571 | 98.7571
| 500 | 0.5 | 1.1 | 1.4 | 1.54 | 3.14 | 4.8356 | 0.55412 | 19.55 | 10.8331 | 0.78963 | 2.23 | 1.7609 | 2.8 | 5.67 | 15.876 | 17.4296 | 0.75038 | 3.9867 | 37.2923 | 70.24 | 408 | 10.2 | 117.7323 | 135.3922 | 105 | 103 | 22 | 240.3922 | 238.3922 | 157.3922
| 600 | 0.6 | 1.2 | 1.5 | 1.8 | 3.14 | 5.652 | 0.62088 | 19.55 | 12.1382 | 0.89652 | 2.23 | 1.9992 | 3 | 5.67 | 17.01 | 19.7894 | 0.90348 | 4.8002 | 41.5996 | 87.89 | 408 | 10.2 | 139.6896 | 160.6431 | 123 | 121 | 26 | 283.6431 | 281.6431 | 186.6431
| 700 | 0.7 | 1.3 | 1.6 | 2.08 | 3.14 | 6.5312 | 0.66995 | 19.55 | 13.0976 | 1.0254 | 2.23 | 2.2866 | 3.2 | 5.67 | 18.144 | 21.9155 | 1.0546 | 5.6031 | 45.6626 | 114.2 | 492 | 12.3 | 172.1626 | 197.987 | 123 | 121 | 26 | 320.987 | 318.987 | 223.987
| 800 | 0.8 | 1.4 | 1.7 | 2.38 | 3.14 | 7.4732 | 0.69664 | 19.55 | 13.6193 | 1.181 | 2.23 | 2.6335 | 3.4 | 5.67 | 19.278 | 23.7261 | 1.199 | 6.3705 | 49.3746 | 140.9 | 492 | 12.3 | 202.5746 | 232.9607 | 145 | 143 | 30 | 377.9607 | 375.9607 | 262.9607
| 900 | 0.9 | 1.5 | 1.8 | 2.7 | 3.14 | 8.478 | 0.69623 | 19.55 | 13.6112 | 1.3679 | 2.23 | 3.0505 | 3.6 | 5.67 | 20.412 | 25.1397 | 1.3321 | 7.0773 | 52.629 | 149 | 492 | 12.3 | 213.929 | 246.0183 | 145 | 143 | 30 | 391.0183 | 389.0183 | 276.0183
| 1000 | 1 | 1.6 | 1.9 | 3.04 | 3.14 | 9.5456 | 0.664 | 19.55 | 12.9812 | 1.591 | 2.23 | 3.5479 | 3.8 | 5.67 | 21.546 | 26.0747 | 1.449 | 7.6985 | 55.3193 | 166.5 | 492 | 12.3 | 234.1193 | 269.2372 | 171 | 169 | 34 | 440.2372 | 438.2372 | 303.2372
| 1250 | 1.25 | 1.85 | 2.15 | 3.9775 | 3.14 | 12.4893 | 0.41336 | 19.55 | 8.0812 | 2.3376 | 2.23 | 5.2128 | 4.3 | 5.67 | 24.381 | 25.7833 | 1.6399 | 8.7129 | 58.8772 | 203.43 | 492 | 12.3 | 274.6072 | 315.7983 | 171 | 169 | 34 | 486.7983 | 484.7983 | 349.7983
Hg = 1.5 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDEN-TAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 1.56 | 1.1856 | 3.14 | 3.7228 | 0.25833 | 19.55 | 5.0503 | 0.90718 | 2.23 | 2.023 | 3.12 | 5.67 | 17.6904 | 10.7961 | 0.27842 | 1.4793 | 29.9657 | 9.87 | 408 | 10.2 | 50.0357 | 57.5411 | 73 | 72 | 15 | 130.5411 | 129.5411 | 72.5411
| 200 | 0.2 | 0.8 | 1.6 | 1.28 | 3.14 | 4.0192 | 0.29488 | 19.55 | 5.7649 | 0.95372 | 2.23 | 2.1268 | 3.2 | 5.67 | 18.144 | 11.9109 | 0.32628 | 1.7335 | 31.7884 | 11.9 | 408 | 10.2 | 53.8884 | 61.9717 | 82 | 81 | 17 | 143.9717 | 142.9717 | 78.9717
| 250 | 0.25 | 0.85 | 1.65 | 1.4025 | 3.14 | 4.4039 | 0.3408 | 19.55 | 6.6626 | 1.0126 | 2.23 | 2.2582 | 3.3 | 5.67 | 18.711 | 13.3246 | 0.38986 | 2.0713 | 34.1069 | 17 | 408 | 10.2 | 61.3069 | 70.503 | 82 | 81 | 17 | 152.503 | 151.503 | 87.503
| 300 | 0.315 | 0.915 | 1.715 | 1.5692 | 3.14 | 4.9274 | 0.39995 | 19.55 | 7.8191 | 1.0914 | 2.23 | 2.4338 | 3.43 | 5.67 | 19.4481 | 15.1802 | 0.47785 | 2.5388 | 37.1671 | 24.68 | 408 | 10.2 | 72.0471 | 82.8542 | 91 | 90 | 19 | 173.8542 | 172.8542 | 101.8542
| 355 | 0.355 | 0.955 | 1.755 | 1.676 | 3.14 | 5.2627 | 0.43555 | 19.55 | 8.5149 | 1.1415 | 2.23 | 2.5457 | 3.51 | 5.67 | 19.9017 | 16.3233 | 0.53448 | 2.8397 | 39.0647 | 31.35 | 408 | 10.2 | 80.6147 | 92.7069 | 91 | 90 | 19 | 183.7069 | 182.7069 | 111.7069
| 400 | 0.4 | 1 | 1.8 | 1.8 | 3.14 | 5.652 | 0.4744 | 19.55 | 9.2745 | 1.2 | 2.23 | 2.676 | 3.6 | 5.67 | 20.412 | 17.6025 | 0.6 | 3.1878 | 41.2023 | 38.44 | 408 | 10.2 | 89.8423 | 103.3187 | 105 | 103 | 22 | 208.3187 | 206.3187 | 125.3187
| 500 | 0.5 | 1.1 | 1.9 | 2.09 | 3.14 | 6.5626 | 0.55412 | 19.55 | 10.8331 | 1.3396 | 2.23 | 2.9874 | 3.8 | 5.67 | 21.546 | 20.3831 | 0.75038 | 3.9867 | 45.9158 | 70.24 | 408 | 10.2 | 126.3558 | 145.3092 | 105 | 103 | 22 | 250.3092 | 248.3092 | 167.3092
| 600 | 0.6 | 1.2 | 2 | 2.4 | 3.14 | 7.536 | 0.62088 | 19.55 | 12.1382 | 1.4965 | 2.23 | 3.3372 | 4 | 5.67 | 22.68 | 23.0114 | 0.90348 | 4.8002 | 50.4916 | 87.89 | 408 | 10.2 | 148.5816 | 170.8689 | 123 | 121 | 26 | 293.8689 | 291.8689 | 196.8689
| 700 | 0.7 | 1.3 | 2.1 | 2.73 | 3.14 | 8.5722 | 0.66995 | 19.55 | 13.0976 | 1.6754 | 2.23 | 3.7361 | 4.2 | 5.67 | 23.814 | 25.406 | 1.0546 | 5.6031 | 54.8231 | 114.2 | 492 | 12.3 | 181.3231 | 208.5215 | 123 | 121 | 26 | 331.5215 | 329.5215 | 234.5215
| 800 | 0.8 | 1.4 | 2.2 | 3.08 | 3.14 | 9.6712 | 0.69664 | 19.55 | 13.6193 | 1.881 | 2.23 | 4.1945 | 4.4 | 5.67 | 24.948 | 27.4851 | 1.199 | 6.3705 | 58.8036 | 140.9 | 492 | 12.3 | 212.0036 | 243.8041 | 145 | 143 | 30 | 388.8041 | 386.8041 | 273.8041
| 900 | 0.9 | 1.5 | 2.3 | 3.45 | 3.14 | 10.833 | 0.69623 | 19.55 | 13.6112 | 2.1179 | 2.23 | 4.723 | 4.6 | 5.67 | 26.082 | 29.1672 | 1.3321 | 7.0773 | 62.3265 | 149 | 492 | 12.3 | 223.6265 | 257.1705 | 145 | 143 | 30 | 402.1705 | 400.1705 | 287.1705
| 1000 | 1 | 1.6 | 2.4 | 3.84 | 3.14 | 12.0576 | 0.664 | 19.55 | 12.9812 | 2.391 | 2.23 | 5.3319 | 4.8 | 5.67 | 27.216 | 30.3707 | 1.449 | 7.6985 | 65.2853 | 166.5 | 492 | 12.3 | 244.0853 | 280.6981 | 171 | 169 | 34 | 451.6981 | 449.6981 | 314.6981
| 1250 | 1.25 | 1.85 | 2.65 | 4.9025 | 3.14 | 15.3939 | 0.41336 | 19.55 | 8.0812 | 3.2626 | 2.23 | 7.2755 | 5.3 | 5.67 | 30.051 | 30.7506 | 1.6399 | 8.7129 | 69.5145 | 203.43 | 492 | 12.3 | 285.2445 | 328.0312 | 171 | 169 | 34 | 499.0312 | 497.0312 | 362.0312
Hg = 2 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 2.06 | 1.5656 | 3.14 | 4.916 | 0.25833 | 19.55 | 5.0503 | 1.2872 | 2.23 | 2.8704 | 4.12 | 5.67 | 23.3604 | 12.8367 | 0.27842 | 1.4793 | 37.6763 | 9.87 | 757 | 18.925 | 66.4713 | 76.442 | 73 | 72 | 15 | 149.442 | 148.442 | 91.442
| 200 | 0.2 | 0.8 | 2.1 | 1.68 | 3.14 | 5.2752 | 0.29488 | 19.55 | 5.7649 | 1.3537 | 2.23 | 3.0188 | 4.2 | 5.67 | 23.814 | 14.0589 | 0.32628 | 1.7335 | 39.6064 | 11.9 | 757 | 18.925 | 70.4314 | 80.9961 | 82 | 81 | 17 | 162.9961 | 161.9961 | 97.9961
| 250 | 0.25 | 0.85 | 2.15 | 1.8275 | 3.14 | 5.7383 | 0.3408 | 19.55 | 6.6626 | 1.4376 | 2.23 | 3.2059 | 4.3 | 5.67 | 24.381 | 15.6069 | 0.38986 | 2.0713 | 42.0592 | 17 | 757 | 18.925 | 77.9842 | 89.6818 | 82 | 81 | 17 | 171.6818 | 170.6818 | 106.6818
| 300 | 0.315 | 0.915 | 2.215 | 2.0267 | 3.14 | 6.3639 | 0.39995 | 19.55 | 7.8191 | 1.5489 | 2.23 | 3.454 | 4.43 | 5.67 | 25.1181 | 17.637 | 0.47785 | 2.5388 | 45.2939 | 24.68 | 757 | 18.925 | 88.8989 | 102.2338 | 91 | 90 | 19 | 193.2338 | 192.2338 | 121.2338
| 355 | 0.355 | 0.955 | 2.255 | 2.1535 | 3.14 | 6.7621 | 0.43555 | 19.55 | 8.5149 | 1.619 | 2.23 | 3.6105 | 4.51 | 5.67 | 25.5717 | 18.8875 | 0.53448 | 2.8397 | 47.2989 | 31.35 | 757 | 18.925 | 97.5739 | 112.2099 | 91 | 90 | 19 | 203.2099 | 202.2099 | 131.2099
| 400 | 0.4 | 1 | 2.3 | 2.3 | 3.14 | 7.222 | 0.4744 | 19.55 | 9.2745 | 1.7 | 2.23 | 3.791 | 4.6 | 5.67 | 26.082 | 20.2875 | 0.6 | 3.1878 | 49.5573 | 38.44 | 757 | 18.925 | 106.9223 | 122.9607 | 105 | 103 | 22 | 227.9607 | 225.9607 | 144.9607
| 500 | 0.5 | 1.1 | 2.4 | 2.64 | 3.14 | 8.2896 | 0.55412 | 19.55 | 10.8331 | 1.8896 | 2.23 | 4.2139 | 4.8 | 5.67 | 27.216 | 23.3366 | 0.75038 | 3.9867 | 54.5393 | 70.24 | 757 | 18.925 | 143.7043 | 165.26 | 105 | 103 | 22 | 270.26 | 268.26 | 187.26
| 600 | 0.6 | 1.2 | 2.5 | 3 | 3.14 | 9.42 | 0.62088 | 19.55 | 12.1382 | 2.0965 | 2.23 | 4.6752 | 5 | 5.67 | 28.35 | 26.2334 | 0.90348 | 4.8002 | 59.3836 | 87.89 | 757 | 18.925 | 166.1986 | 191.1284 | 123 | 121 | 26 | 314.1284 | 312.1284 | 217.1284
| 700 | 0.7 | 1.3 | 2.6 | 3.38 | 3.14 | 10.6132 | 0.66995 | 19.55 | 13.0976 | 2.3254 | 2.23 | 5.1856 | 5.2 | 5.67 | 29.484 | 28.8965 | 1.0546 | 5.6031 | 63.9836 | 114.2 | 989 | 24.725 | 202.9086 | 233.3449 | 123 | 121 | 26 | 356.3449 | 354.3449 | 259.3449
| 800 | 0.8 | 1.4 | 2.7 | 3.78 | 3.14 | 11.8692 | 0.69664 | 19.55 | 13.6193 | 2.581 | 2.23 | 5.7555 | 5.4 | 5.67 | 30.618 | 31.2441 | 1.199 | 6.3705 | 68.2326 | 140.9 | 989 | 24.725 | 233.8576 | 268.9362 | 145 | 143 | 30 | 413.9362 | 411.9362 | 298.9362
| 900 | 0.9 | 1.5 | 2.8 | 4.2 | 3.14 | 13.188 | 0.69623 | 19.55 | 13.6112 | 2.8679 | 2.23 | 6.3955 | 5.6 | 5.67 | 31.752 | 33.1947 | 1.3321 | 7.0773 | 72.024 | 149 | 989 | 24.725 | 245.749 | 282.6113 | 145 | 143 | 30 | 427.6113 | 425.6113 | 312.6113
| 1000 | 1 | 1.6 | 2.9 | 4.64 | 3.14 | 14.5696 | 0.664 | 19.55 | 12.9812 | 3.191 | 2.23 | 7.1159 | 5.8 | 5.67 | 32.886 | 34.6667 | 1.449 | 7.6985 | 75.2513 | 166.5 | 989 | 24.725 | 266.4763 | 306.4477 | 171 | 169 | 34 | 477.4477 | 475.4477 | 340.4477
| 1250 | 1.25 | 1.85 | 3.15 | 5.8275 | 3.14 | 18.2983 | 0.41336 | 19.55 | 8.0812 | 4.1876 | 2.23 | 9.3383 | 6.3 | 5.67 | 35.721 | 35.7178 | 1.6399 | 8.7129 | 80.1517 | 203.43 | 989 | 24.725 | 308.3067 | 354.5527 | 171 | 169 | 34 | 525.5527 | 523.5527 | 388.5527
Hg = 2.5 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 2.56 | 1.9456 | 3.14 | 6.1092 | 0.25833 | 19.55 | 5.0503 | 1.6672 | 2.23 | 3.7178 | 5.12 | 5.67 | 29.0304 | 14.8773 | 0.27842 | 1.4793 | 45.3869 | 9.87 | 757 | 18.925 | 74.1819 | 85.3092 | 73 | 72 | 15 | 158.3092 | 157.3092 | 100.3092
| 200 | 0.2 | 0.8 | 2.6 | 2.08 | 3.14 | 6.5312 | 0.29488 | 19.55 | 5.7649 | 1.7537 | 2.23 | 3.9108 | 5.2 | 5.67 | 29.484 | 16.2069 | 0.32628 | 1.7335 | 47.4244 | 11.9 | 757 | 18.925 | 78.2494 | 89.9868 | 82 | 81 | 17 | 171.9868 | 170.9868 | 106.9868
| 250 | 0.25 | 0.85 | 2.65 | 2.2525 | 3.14 | 7.0728 | 0.3408 | 19.55 | 6.6626 | 1.8626 | 2.23 | 4.1537 | 5.3 | 5.67 | 30.051 | 17.8891 | 0.38986 | 2.0713 | 50.0114 | 17 | 757 | 18.925 | 85.9364 | 98.8269 | 82 | 81 | 17 | 180.8269 | 179.8269 | 115.8269
| 300 | 0.315 | 0.915 | 2.715 | 2.4842 | 3.14 | 7.8005 | 0.39995 | 19.55 | 7.8191 | 2.0064 | 2.23 | 4.4742 | 5.43 | 5.67 | 30.7881 | 20.0938 | 0.47785 | 2.5388 | 53.4207 | 24.68 | 757 | 18.925 | 97.0257 | 111.5795 | 91 | 90 | 19 | 202.5795 | 201.5795 | 130.5795
| 355 | 0.355 | 0.955 | 2.755 | 2.631 | 3.14 | 8.2614 | 0.43555 | 19.55 | 8.5149 | 2.0965 | 2.23 | 4.6753 | 5.51 | 5.67 | 31.2417 | 21.4517 | 0.53448 | 2.8397 | 55.533 | 31.35 | 757 | 18.925 | 105.808 | 121.6793 | 91 | 90 | 19 | 212.6793 | 211.6793 | 140.6793
| 400 | 0.4 | 1 | 2.8 | 2.8 | 3.14 | 8.792 | 0.4744 | 19.55 | 9.2745 | 2.2 | 2.23 | 4.906 | 5.6 | 5.67 | 31.752 | 22.9725 | 0.6 | 3.1878 | 57.9123 | 38.44 | 757 | 18.925 | 115.2773 | 132.5689 | 105 | 103 | 22 | 237.5689 | 235.5689 | 154.5689
| 500 | 0.5 | 1.1 | 2.9 | 3.19 | 3.14 | 10.0166 | 0.55412 | 19.55 | 10.8331 | 2.4396 | 2.23 | 5.4404 | 5.8 | 5.67 | 32.886 | 26.2901 | 0.75038 | 3.9867 | 63.1628 | 70.24 | 757 | 18.925 | 152.3278 | 175.177 | 105 | 103 | 22 | 280.177 | 278.177 | 197.177
| 600 | 0.6 | 1.2 | 3 | 3.6 | 3.14 | 11.304 | 0.62088 | 19.55 | 12.1382 | 2.6965 | 2.23 | 6.0132 | 6 | 5.67 | 34.02 | 29.4554 | 0.90348 | 4.8002 | 68.2756 | 87.89 | 757 | 18.925 | 175.0906 | 201.3542 | 123 | 121 | 26 | 324.3542 | 322.3542 | 227.3542
| 700 | 0.7 | 1.3 | 3.1 | 4.03 | 3.14 | 12.6542 | 0.66995 | 19.55 | 13.0976 | 2.9754 | 2.23 | 6.6351 | 6.2 | 5.67 | 35.154 | 32.387 | 1.0546 | 5.6031 | 73.1441 | 114.2 | 989 | 24.725 | 212.0691 | 243.8794 | 123 | 121 | 26 | 366.8794 | 364.8794 | 269.8794
| 800 | 0.8 | 1.4 | 3.2 | 4.48 | 3.14 | 14.0672 | 0.69664 | 19.55 | 13.6193 | 3.281 | 2.23 | 7.3165 | 6.4 | 5.67 | 36.288 | 35.0031 | 1.199 | 6.3705 | 77.6616 | 140.9 | 989 | 24.725 | 243.2866 | 279.7795 | 145 | 143 | 30 | 424.7795 | 422.7795 | 309.7795
| 900 | 0.9 | 1.5 | 3.3 | 4.95 | 3.14 | 15.543 | 0.69623 | 19.55 | 13.6112 | 3.6179 | 2.23 | 8.068 | 6.6 | 5.67 | 37.422 | 37.2222 | 1.3321 | 7.0773 | 81.7215 | 149 | 989 | 24.725 | 255.4465 | 293.7635 | 145 | 143 | 30 | 438.7635 | 436.7635 | 323.7635
| 1000 | 1 | 1.6 | 3.4 | 5.44 | 3.14 | 17.0816 | 0.664 | 19.55 | 12.9812 | 3.991 | 2.23 | 8.8999 | 6.8 | 5.67 | 38.556 | 38.9627 | 1.449 | 7.6985 | 85.2173 | 166.5 | 989 | 24.725 | 276.4423 | 317.9086 | 171 | 169 | 34 | 488.9086 | 486.9086 | 351.9086
| 1250 | 1.25 | 1.85 | 3.65 | 6.7525 | 3.14 | 21.2029 | 0.41336 | 19.55 | 8.0812 | 5.1126 | 2.23 | 11.401 | 7.3 | 5.67 | 41.391 | 40.6851 | 1.6399 | 8.7129 | 90.789 | 203.43 | 989 | 24.725 | 318.944 | 366.7856 | 171 | 169 | 34 | 537.7856 | 535.7856 | 400.7856
Hg =3 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 3.06 | 2.3256 | 3.14 | 7.3024 | 0.25833 | 19.55 | 5.0503 | 2.0472 | 2.23 | 4.5652 | 6.12 | 5.67 | 34.7004 | 16.9179 | 0.27842 | 1.4793 | 53.0975 | 9.87 | 757 | 18.925 | 81.8925 | 94.1764 | 73 | 72 | 15 | 167.1764 | 166.1764 | 109.1764
| 200 | 0.2 | 0.8 | 3.1 | 2.48 | 3.14 | 7.7872 | 0.29488 | 19.55 | 5.7649 | 2.1537 | 2.23 | 4.8028 | 6.2 | 5.67 | 35.154 | 18.3549 | 0.32628 | 1.7335 | 55.2424 | 11.9 | 757 | 18.925 | 86.0674 | 98.9775 | 82 | 81 | 17 | 180.9775 | 179.9775 | 115.9775
| 250 | 0.25 | 0.85 | 3.15 | 2.6775 | 3.14 | 8.4073 | 0.3408 | 19.55 | 6.6626 | 2.2876 | 2.23 | 5.1014 | 6.3 | 5.67 | 35.721 | 20.1714 | 0.38986 | 2.0713 | 57.9637 | 17 | 757 | 18.925 | 93.8887 | 107.972 | 82 | 81 | 17 | 189.972 | 188.972 | 124.972
| 300 | 0.315 | 0.915 | 3.215 | 2.9417 | 3.14 | 9.237 | 0.39995 | 19.55 | 7.8191 | 2.4639 | 2.23 | 5.4945 | 6.43 | 5.67 | 36.4581 | 22.5506 | 0.47785 | 2.5388 | 61.5475 | 24.68 | 757 | 18.925 | 105.1525 | 120.9253 | 91 | 90 | 19 | 211.9253 | 210.9253 | 139.9253
| 355 | 0.355 | 0.955 | 3.255 | 3.1085 | 3.14 | 9.7608 | 0.43555 | 19.55 | 8.5149 | 2.574 | 2.23 | 5.7401 | 6.51 | 5.67 | 36.9117 | 24.0158 | 0.53448 | 2.8397 | 63.7672 | 31.35 | 757 | 18.925 | 114.0422 | 131.1486 | 91 | 90 | 19 | 222.1486 | 221.1486 | 150.1486
| 400 | 0.4 | 1 | 3.3 | 3.3 | 3.14 | 10.362 | 0.4744 | 19.55 | 9.2745 | 2.7 | 2.23 | 6.021 | 6.6 | 5.67 | 37.422 | 25.6575 | 0.6 | 3.1878 | 66.2673 | 38.44 | 757 | 18.925 | 123.6323 | 142.1772 | 105 | 103 | 22 | 247.1772 | 245.1772 | 164.1772
| 500 | 0.5 | 1.1 | 3.4 | 3.74 | 3.14 | 11.7436 | 0.55412 | 19.55 | 10.8331 | 2.9896 | 2.23 | 6.6669 | 6.8 | 5.67 | 38.556 | 29.2436 | 0.75038 | 3.9867 | 71.7863 | 70.24 | 757 | 18.925 | 160.9513 | 185.0941 | 105 | 103 | 22 | 290.0941 | 288.0941 | 207.0941
| 600 | 0.6 | 1.2 | 3.5 | 4.2 | 3.14 | 13.188 | 0.62088 | 19.55 | 12.1382 | 3.2965 | 2.23 | 7.3512 | 7 | 5.67 | 39.69 | 32.6774 | 0.90348 | 4.8002 | 77.1676 | 87.89 | 757 | 18.925 | 183.9826 | 211.58 | 123 | 121 | 26 | 334.58 | 332.58 | 237.58
| 700 | 0.7 | 1.3 | 3.6 | 4.68 | 3.14 | 14.6952 | 0.66995 | 19.55 | 13.0976 | 3.6254 | 2.23 | 8.0846 | 7.2 | 5.67 | 40.824 | 35.8775 | 1.0546 | 5.6031 | 82.3046 | 114.2 | 989 | 24.725 | 221.2296 | 254.414 | 123 | 121 | 26 | 377.414 | 375.414 | 280.414
| 800 | 0.8 | 1.4 | 3.7 | 5.18 | 3.14 | 16.2652 | 0.69664 | 19.55 | 13.6193 | 3.981 | 2.23 | 8.8775 | 7.4 | 5.67 | 41.958 | 38.7621 | 1.199 | 6.3705 | 87.0906 | 140.9 | 989 | 24.725 | 252.7156 | 290.6229 | 145 | 143 | 30 | 435.6229 | 433.6229 | 320.6229
| 900 | 0.9 | 1.5 | 3.8 | 5.7 | 3.14 | 17.898 | 0.69623 | 19.55 | 13.6112 | 4.3679 | 2.23 | 9.7405 | 7.6 | 5.67 | 43.092 | 41.2497 | 1.3321 | 7.0773 | 91.419 | 149 | 989 | 24.725 | 265.144 | 304.9156 | 145 | 143 | 30 | 449.9156 | 447.9156 | 334.9156
| 1000 | 1 | 1.6 | 3.9 | 6.24 | 3.14 | 19.5936 | 0.664 | 19.55 | 12.9812 | 4.791 | 2.23 | 10.6839 | 7.8 | 5.67 | 44.226 | 43.2587 | 1.449 | 7.6985 | 95.1833 | 166.5 | 989 | 24.725 | 286.4083 | 329.3695 | 171 | 169 | 34 | 500.3695 | 498.3695 | 363.3695
| 1250 | 1.25 | 1.85 | 4.15 | 7.6775 | 3.14 | 24.1074 | 0.41336 | 19.55 | 8.0812 | 6.0376 | 2.23 | 13.4638 | 8.3 | 5.67 | 47.061 | 45.6523 | 1.6399 | 8.7129 | 101.4262 | 203.43 | 989 | 24.725 | 329.5812 | 379.0184 | 171 | 169 | 34 | 550.0184 | 548.0184 | 413.0184
Hg =4 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 10% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 4.06 | 3.0856 | 3.14 | 9.6888 | 0.25833 | 19.55 | 5.0503 | 2.8072 | 2.23 | 6.26 | 8.12 | 5.67 | 46.0404 | 20.9991 | 0.27842 | 1.4793 | 68.5187 | 9.87 | 815 | 20.375 | 98.7637 | 108.6401 | 73 | 72 | 15 | 181.6401 | 180.6401 | 123.6401
| 200 | 0.2 | 0.8 | 4.1 | 3.28 | 3.14 | 10.2992 | 0.29488 | 19.55 | 5.7649 | 2.9537 | 2.23 | 6.5868 | 8.2 | 5.67 | 46.494 | 22.6509 | 0.32628 | 1.7335 | 70.8784 | 11.9 | 815 | 20.375 | 103.1534 | 113.4688 | 82 | 81 | 17 | 195.4688 | 194.4688 | 130.4688
| 250 | 0.25 | 0.85 | 4.15 | 3.5275 | 3.14 | 11.0763 | 0.3408 | 19.55 | 6.6626 | 3.1376 | 2.23 | 6.9969 | 8.3 | 5.67 | 47.061 | 24.7359 | 0.38986 | 2.0713 | 73.8682 | 17 | 815 | 20.375 | 111.2432 | 122.3675 | 82 | 81 | 17 | 204.3675 | 203.3675 | 139.3675
| 300 | 0.315 | 0.915 | 4.215 | 3.8567 | 3.14 | 12.1101 | 0.39995 | 19.55 | 7.8191 | 3.3789 | 2.23 | 7.5349 | 8.43 | 5.67 | 47.7981 | 27.4641 | 0.47785 | 2.5388 | 77.801 | 24.68 | 815 | 20.375 | 122.856 | 135.1416 | 91 | 90 | 19 | 226.1416 | 225.1416 | 154.1416
| 355 | 0.355 | 0.955 | 4.255 | 4.0635 | 3.14 | 12.7595 | 0.43555 | 19.55 | 8.5149 | 3.529 | 2.23 | 7.8698 | 8.51 | 5.67 | 48.2517 | 29.1442 | 0.53448 | 2.8397 | 80.2356 | 31.35 | 815 | 20.375 | 131.9606 | 145.1566 | 91 | 90 | 19 | 236.1566 | 235.1566 | 164.1566
| 400 | 0.4 | 1 | 4.3 | 4.3 | 3.14 | 13.502 | 0.4744 | 19.55 | 9.2745 | 3.7 | 2.23 | 8.251 | 8.6 | 5.67 | 48.762 | 31.0275 | 0.6 | 3.1878 | 82.9773 | 38.44 | 815 | 20.375 | 141.7923 | 155.9716 | 105 | 103 | 22 | 260.9716 | 258.9716 | 177.9716
| 500 | 0.5 | 1.1 | 4.4 | 4.84 | 3.14 | 15.1976 | 0.55412 | 19.55 | 10.8331 | 4.0896 | 2.23 | 9.1199 | 8.8 | 5.67 | 49.896 | 35.1506 | 0.75038 | 3.9867 | 89.0333 | 70.24 | 815 | 20.375 | 179.6483 | 197.6132 | 105 | 103 | 22 | 302.6132 | 300.6132 | 219.6132
| 600 | 0.6 | 1.2 | 4.5 | 5.4 | 3.14 | 16.956 | 0.62088 | 19.55 | 12.1382 | 4.4965 | 2.23 | 10.0272 | 9 | 5.67 | 51.03 | 39.1214 | 0.90348 | 4.8002 | 94.9516 | 87.89 | 815 | 20.375 | 203.2166 | 223.5383 | 123 | 121 | 26 | 346.5383 | 344.5383 | 249.5383
| 700 | 0.7 | 1.3 | 4.6 | 5.98 | 3.14 | 18.7772 | 0.66995 | 19.55 | 13.0976 | 4.9254 | 2.23 | 10.9836 | 9.2 | 5.67 | 52.164 | 42.8585 | 1.0546 | 5.6031 | 100.6256 | 114.2 | 1047 | 26.175 | 241.0006 | 265.1006 | 123 | 121 | 26 | 388.1006 | 386.1006 | 291.1006
| 800 | 0.8 | 1.4 | 4.7 | 6.58 | 3.14 | 20.6612 | 0.69664 | 19.55 | 13.6193 | 5.381 | 2.23 | 11.9995 | 9.4 | 5.67 | 53.298 | 46.2801 | 1.199 | 6.3705 | 105.9486 | 140.9 | 1047 | 26.175 | 273.0236 | 300.3259 | 145 | 143 | 30 | 445.3259 | 443.3259 | 330.3259
| 900 | 0.9 | 1.5 | 4.8 | 7.2 | 3.14 | 22.608 | 0.69623 | 19.55 | 13.6112 | 5.8679 | 2.23 | 13.0855 | 9.6 | 5.67 | 54.432 | 49.3047 | 1.3321 | 7.0773 | 110.814 | 149 | 1047 | 26.175 | 285.989 | 314.5879 | 145 | 143 | 30 | 459.5879 | 457.5879 | 344.5879
| 1000 | 1 | 1.6 | 4.9 | 7.84 | 3.14 | 24.6176 | 0.664 | 19.55 | 12.9812 | 6.391 | 2.23 | 14.2519 | 9.8 | 5.67 | 55.566 | 51.8507 | 1.449 | 7.6985 | 115.1153 | 166.5 | 1047 | 26.175 | 307.7903 | 338.5693 | 171 | 169 | 34 | 509.5693 | 507.5693 | 372.5693
| 1250 | 1.25 | 1.85 | 5.15 | 9.5275 | 3.14 | 29.9164 | 0.41336 | 19.55 | 8.0812 | 7.8876 | 2.23 | 17.5893 | 10.3 | 5.67 | 58.401 | 55.5868 | 1.6399 | 8.7129 | 122.7007 | 203.43 | 1047 | 26.175 | 352.3057 | 387.5363 | 171 | 169 | 34 | 558.5363 | 556.5363 | 421.5363
Hg =5 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 10% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 5.06 | 3.8456 | 3.14 | 12.0752 | 0.25833 | 19.55 | 5.0503 | 3.5672 | 2.23 | 7.9548 | 10.12 | 5.67 | 57.3804 | 25.0803 | 0.27842 | 1.4793 | 83.9399 | 9.87 | 815 | 20.375 | 114.1849 | 125.6034 | 73 | 72 | 15 | 198.6034 | 197.6034 | 140.6034
| 200 | 0.2 | 0.8 | 5.1 | 4.08 | 3.14 | 12.8112 | 0.29488 | 19.55 | 5.7649 | 3.7537 | 2.23 | 8.3708 | 10.2 | 5.67 | 57.834 | 26.9469 | 0.32628 | 1.7335 | 86.5144 | 11.9 | 815 | 20.375 | 118.7894 | 130.6684 | 82 | 81 | 17 | 212.6684 | 211.6684 | 147.6684
| 250 | 0.25 | 0.85 | 5.15 | 4.3775 | 3.14 | 13.7453 | 0.3408 | 19.55 | 6.6626 | 3.9876 | 2.23 | 8.8924 | 10.3 | 5.67 | 58.401 | 29.3004 | 0.38986 | 2.0713 | 89.7727 | 17 | 815 | 20.375 | 127.1477 | 139.8625 | 82 | 81 | 17 | 221.8625 | 220.8625 | 156.8625
| 300 | 0.315 | 0.915 | 5.215 | 4.7717 | 3.14 | 14.9832 | 0.39995 | 19.55 | 7.8191 | 4.2939 | 2.23 | 9.5754 | 10.43 | 5.67 | 59.1381 | 32.3777 | 0.47785 | 2.5388 | 94.0546 | 24.68 | 815 | 20.375 | 139.1096 | 153.0205 | 91 | 90 | 19 | 244.0205 | 243.0205 | 172.0205
| 355 | 0.355 | 0.955 | 5.255 | 5.0185 | 3.14 | 15.7582 | 0.43555 | 19.55 | 8.5149 | 4.484 | 2.23 | 9.9994 | 10.51 | 5.67 | 59.5917 | 34.2725 | 0.53448 | 2.8397 | 96.7039 | 31.35 | 815 | 20.375 | 148.4289 | 163.2718 | 91 | 90 | 19 | 254.2718 | 253.2718 | 182.2718
| 400 | 0.4 | 1 | 5.3 | 5.3 | 3.14 | 16.642 | 0.4744 | 19.55 | 9.2745 | 4.7 | 2.23 | 10.481 | 10.6 | 5.67 | 60.102 | 36.3975 | 0.6 | 3.1878 | 99.6873 | 38.44 | 815 | 20.375 | 158.5023 | 174.3526 | 105 | 103 | 22 | 279.3526 | 277.3526 | 196.3526
| 500 | 0.5 | 1.1 | 5.4 | 5.94 | 3.14 | 18.6516 | 0.55412 | 19.55 | 10.8331 | 5.1896 | 2.23 | 11.5729 | 10.8 | 5.67 | 61.236 | 41.0576 | 0.75038 | 3.9867 | 106.2803 | 70.24 | 815 | 20.375 | 196.8953 | 216.5849 | 105 | 103 | 22 | 321.5849 | 319.5849 | 238.5849
| 600 | 0.6 | 1.2 | 5.5 | 6.6 | 3.14 | 20.724 | 0.62088 | 19.55 | 12.1382 | 5.6965 | 2.23 | 12.7032 | 11 | 5.67 | 62.37 | 45.5654 | 0.90348 | 4.8002 | 112.7356 | 87.89 | 815 | 20.375 | 221.0006 | 243.1007 | 123 | 121 | 26 | 366.1007 | 364.1007 | 269.1007
| 700 | 0.7 | 1.3 | 5.6 | 7.28 | 3.14 | 22.8592 | 0.66995 | 19.55 | 13.0976 | 6.2254 | 2.23 | 13.8826 | 11.2 | 5.67 | 63.504 | 49.8395 | 1.0546 | 5.6031 | 118.9466 | 114.2 | 1047 | 26.175 | 259.3216 | 285.2537 | 123 | 121 | 26 | 408.2537 | 406.2537 | 311.2537
| 800 | 0.8 | 1.4 | 5.7 | 7.98 | 3.14 | 25.0572 | 0.69664 | 19.55 | 13.6193 | 6.781 | 2.23 | 15.1215 | 11.4 | 5.67 | 64.638 | 53.7981 | 1.199 | 6.3705 | 124.8066 | 140.9 | 1047 | 26.175 | 291.8816 | 321.0697 | 145 | 143 | 30 | 466.0697 | 464.0697 | 351.0697
| 900 | 0.9 | 1.5 | 5.8 | 8.7 | 3.14 | 27.318 | 0.69623 | 19.55 | 13.6112 | 7.3679 | 2.23 | 16.4305 | 11.6 | 5.67 | 65.772 | 57.3597 | 1.3321 | 7.0773 | 130.209 | 149 | 1047 | 26.175 | 305.384 | 335.9224 | 145 | 143 | 30 | 480.9224 | 478.9224 | 365.9224
| 1000 | 1 | 1.6 | 5.9 | 9.44 | 3.14 | 29.6416 | 0.664 | 19.55 | 12.9812 | 7.991 | 2.23 | 17.8199 | 11.8 | 5.67 | 66.906 | 60.4427 | 1.449 | 7.6985 | 135.0473 | 166.5 | 1047 | 26.175 | 327.7223 | 360.4945 | 171 | 169 | 34 | 531.4945 | 529.4945 | 394.4945
| 1250 | 1.25 | 1.85 | 6.15 | 11.3775 | 3.14 | 35.7253 | 0.41336 | 19.55 | 8.0812 | 9.7376 | 2.23 | 21.7148 | 12.3 | 5.67 | 69.741 | 65.5213 | 1.6399 | 8.7129 | 143.9752 | 203.43 | 1047 | 26.175 | 373.5802 | 410.9383 | 171 | 169 | 34 | 581.9383 | 579.9383 | 444.9383
Hg =6 m ADINCIME GENERATOARE SUPERIOARA CONDUCTA
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 10% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 6.06 | 4.6056 | 3.14 | 14.4616 | 0.25833 | 19.55 | 5.0503 | 4.3272 | 2.23 | 9.6496 | 12.12 | 5.67 | 68.7204 | 29.1615 | 0.27842 | 1.4793 | 99.3611 | 9.87 | 815 | 20.375 | 129.6061 | 142.5668 | 73 | 72 | 15 | 215.5668 | 214.5668 | 157.5668
| 200 | 0.2 | 0.8 | 6.1 | 4.88 | 3.14 | 15.3232 | 0.29488 | 19.55 | 5.7649 | 4.5537 | 2.23 | 10.1548 | 12.2 | 5.67 | 69.174 | 31.2429 | 0.32628 | 1.7335 | 102.1504 | 11.9 | 815 | 20.375 | 134.4254 | 147.868 | 82 | 81 | 17 | 229.868 | 228.868 | 164.868
| 250 | 0.25 | 0.85 | 6.15 | 5.2275 | 3.14 | 16.4143 | 0.3408 | 19.55 | 6.6626 | 4.8376 | 2.23 | 10.7879 | 12.3 | 5.67 | 69.741 | 33.8649 | 0.38986 | 2.0713 | 105.6772 | 17 | 815 | 20.375 | 143.0522 | 157.3574 | 82 | 81 | 17 | 239.3574 | 238.3574 | 174.3574
| 300 | 0.315 | 0.915 | 6.215 | 5.6867 | 3.14 | 17.8563 | 0.39995 | 19.55 | 7.8191 | 5.2089 | 2.23 | 11.6158 | 12.43 | 5.67 | 70.4781 | 37.2912 | 0.47785 | 2.5388 | 110.3081 | 24.68 | 815 | 20.375 | 155.3631 | 170.8994 | 91 | 90 | 19 | 261.8994 | 260.8994 | 189.8994
| 355 | 0.355 | 0.955 | 6.255 | 5.9735 | 3.14 | 18.7569 | 0.43555 | 19.55 | 8.5149 | 5.439 | 2.23 | 12.1291 | 12.51 | 5.67 | 70.9317 | 39.4009 | 0.53448 | 2.8397 | 113.1723 | 31.35 | 815 | 20.375 | 164.8973 | 181.387 | 91 | 90 | 19 | 272.387 | 271.387 | 200.387
| 400 | 0.4 | 1 | 6.3 | 6.3 | 3.14 | 19.782 | 0.4744 | 19.55 | 9.2745 | 5.7 | 2.23 | 12.711 | 12.6 | 5.67 | 71.442 | 41.7675 | 0.6 | 3.1878 | 116.3973 | 38.44 | 815 | 20.375 | 175.2123 | 192.7336 | 105 | 103 | 22 | 297.7336 | 295.7336 | 214.7336
| 500 | 0.5 | 1.1 | 6.4 | 7.04 | 3.14 | 22.1056 | 0.55412 | 19.55 | 10.8331 | 6.2896 | 2.23 | 14.0259 | 12.8 | 5.67 | 72.576 | 46.9646 | 0.75038 | 3.9867 | 123.5273 | 70.24 | 815 | 20.375 | 214.1423 | 235.5566 | 105 | 103 | 22 | 340.5566 | 338.5566 | 257.5566
| 600 | 0.6 | 1.2 | 6.5 | 7.8 | 3.14 | 24.492 | 0.62088 | 19.55 | 12.1382 | 6.8965 | 2.23 | 15.3792 | 13 | 5.67 | 73.71 | 52.0094 | 0.90348 | 4.8002 | 130.5196 | 87.89 | 815 | 20.375 | 238.7846 | 262.6631 | 123 | 121 | 26 | 385.6631 | 383.6631 | 288.6631
| 700 | 0.7 | 1.3 | 6.6 | 8.58 | 3.14 | 26.9412 | 0.66995 | 19.55 | 13.0976 | 7.5254 | 2.23 | 16.7816 | 13.2 | 5.67 | 74.844 | 56.8205 | 1.0546 | 5.6031 | 137.2676 | 114.2 | 1047 | 26.175 | 277.6426 | 305.4068 | 123 | 121 | 26 | 428.4068 | 426.4068 | 331.4068
| 800 | 0.8 | 1.4 | 6.7 | 9.38 | 3.14 | 29.4532 | 0.69664 | 19.55 | 13.6193 | 8.181 | 2.23 | 18.2435 | 13.4 | 5.67 | 75.978 | 61.3161 | 1.199 | 6.3705 | 143.6646 | 140.9 | 1047 | 26.175 | 310.7396 | 341.8135 | 145 | 143 | 30 | 486.8135 | 484.8135 | 371.8135
| 900 | 0.9 | 1.5 | 6.8 | 10.2 | 3.14 | 32.028 | 0.69623 | 19.55 | 13.6112 | 8.8679 | 2.23 | 19.7755 | 13.6 | 5.67 | 77.112 | 65.4147 | 1.3321 | 7.0773 | 149.604 | 149 | 1047 | 26.175 | 324.779 | 357.2569 | 145 | 143 | 30 | 502.2569 | 500.2569 | 387.2569
| 1000 | 1 | 1.6 | 6.9 | 11.04 | 3.14 | 34.6656 | 0.664 | 19.55 | 12.9812 | 9.591 | 2.23 | 21.3879 | 13.8 | 5.67 | 78.246 | 69.0347 | 1.449 | 7.6985 | 154.9793 | 166.5 | 1047 | 26.175 | 347.6543 | 382.4197 | 171 | 169 | 34 | 553.4197 | 551.4197 | 416.4197
| 1250 | 1.25 | 1.85 | 7.15 | 13.2275 | 3.14 | 41.5343 | 0.41336 | 19.55 | 8.0812 | 11.5876 | 2.23 | 25.8403 | 14.3 | 5.67 | 81.081 | 75.4558 | 1.6399 | 8.7129 | 165.2497 | 203.43 | 1047 | 26.175 | 394.8547 | 434.3402 | 171 | 169 | 34 | 605.3402 | 603.3402 | 468.3402

## COND CANAL H=1.5M (hidden)
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [28 empty] | 1
| ADINCIME GENERATOARE SUPERIOARA CONDUCTA Hg = | [7 empty] | 1.5 | m
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDEN-TAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 1.56 | 1.1856 | 3.14 | 3.7228 | 0.25833 | 19.55 | 5.0503 | 0.90718 | 2.23 | 2.023 | 3.12 | 5.67 | 17.6904 | 10.7961 | 0.27842 | 1.4793 | 29.9657 | 9.87 | 408 | 10.2 | 50.0357 | 57.5 | 73 | 72 | 15 | 130.5 | 129.5 | 72.5
| 200 | 0.2 | 0.8 | 1.6 | 1.28 | 3.14 | 4.0192 | 0.29488 | 19.55 | 5.7649 | 0.95372 | 2.23 | 2.1268 | 3.2 | 5.67 | 18.144 | 11.9109 | 0.32628 | 1.7335 | 31.7884 | 11.9 | 408 | 10.2 | 53.8884 | 62 | 82 | 81 | 17 | 144 | 143 | 79
| 250 | 0.25 | 0.85 | 1.65 | 1.4025 | 3.14 | 4.4039 | 0.3408 | 19.55 | 6.6626 | 1.0126 | 2.23 | 2.2582 | 3.3 | 5.67 | 18.711 | 13.3246 | 0.38986 | 2.0713 | 34.1069 | 17 | 408 | 10.2 | 61.3069 | 70.5 | 82 | 81 | 17 | 152.5 | 151.5 | 87.5
| 300 | 0.315 | 0.915 | 1.715 | 1.5692 | 3.14 | 4.9274 | 0.39995 | 19.55 | 7.8191 | 1.0914 | 2.23 | 2.4338 | 3.43 | 5.67 | 19.4481 | 15.1802 | 0.47785 | 2.5388 | 37.1671 | 24.68 | 408 | 10.2 | 72.0471 | 82.9 | 91 | 90 | 19 | 173.9 | 172.9 | 101.9
| 355 | 0.355 | 0.955 | 1.755 | 1.676 | 3.14 | 5.2627 | 0.43555 | 19.55 | 8.5149 | 1.1415 | 2.23 | 2.5457 | 3.51 | 5.67 | 19.9017 | 16.3233 | 0.53448 | 2.8397 | 39.0647 | 31.35 | 408 | 10.2 | 80.6147 | 92.7 | 91 | 90 | 19 | 183.7 | 182.7 | 111.7
| 400 | 0.4 | 1 | 1.8 | 1.8 | 3.14 | 5.652 | 0.4744 | 19.55 | 9.2745 | 1.2 | 2.23 | 2.676 | 3.6 | 5.67 | 20.412 | 17.6025 | 0.6 | 3.1878 | 41.2023 | 38.44 | 408 | 10.2 | 89.8423 | 103.3 | 105 | 103 | 22 | 208.3 | 206.3 | 125.3
| 500 | 0.5 | 1.1 | 1.9 | 2.09 | 3.14 | 6.5626 | 0.55412 | 19.55 | 10.8331 | 1.3396 | 2.23 | 2.9874 | 3.8 | 5.67 | 21.546 | 20.3831 | 0.75038 | 3.9867 | 45.9158 | 70.24 | 408 | 10.2 | 126.3558 | 145.3 | 105 | 103 | 22 | 250.3 | 248.3 | 167.3
| 600 | 0.6 | 1.2 | 2 | 2.4 | 3.14 | 7.536 | 0.62088 | 19.55 | 12.1382 | 1.4965 | 2.23 | 3.3372 | 4 | 5.67 | 22.68 | 23.0114 | 0.90348 | 4.8002 | 50.4916 | 87.89 | 408 | 10.2 | 148.5816 | 170.7 | 123 | 121 | 26 | 293.7 | 291.7 | 196.7
| 700 | 0.7 | 1.3 | 2.1 | 2.73 | 3.14 | 8.5722 | 0.66995 | 19.55 | 13.0976 | 1.6754 | 2.23 | 3.7361 | 4.2 | 5.67 | 23.814 | 25.406 | 1.0546 | 5.6031 | 54.8231 | 114.2 | 492 | 12.3 | 181.3231 | 208.5 | 123 | 121 | 26 | 331.5 | 329.5 | 234.5
| 800 | 0.8 | 1.4 | 2.2 | 3.08 | 3.14 | 9.6712 | 0.69664 | 19.55 | 13.6193 | 1.881 | 2.23 | 4.1945 | 4.4 | 5.67 | 24.948 | 27.4851 | 1.199 | 6.3705 | 58.8036 | 140.9 | 492 | 12.3 | 212.0036 | 243.8 | 145 | 143 | 30 | 388.8 | 386.8 | 273.8
| 900 | 0.9 | 1.5 | 2.3 | 3.45 | 3.14 | 10.833 | 0.69623 | 19.55 | 13.6112 | 2.1179 | 2.23 | 4.723 | 4.6 | 5.67 | 26.082 | 29.1672 | 1.3321 | 7.0773 | 62.3265 | 149 | 492 | 12.3 | 223.6265 | 257.2 | 145 | 143 | 30 | 402.2 | 400.2 | 287.2
| 1000 | 1 | 1.6 | 2.4 | 3.84 | 3.14 | 12.0576 | 0.664 | 19.55 | 12.9812 | 2.391 | 2.23 | 5.3319 | 4.8 | 5.67 | 27.216 | 30.3707 | 1.449 | 7.6985 | 65.2853 | 166.5 | 492 | 12.3 | 244.0853 | 280.7 | 171 | 169 | 34 | 451.7 | 449.7 | 314.7
| 1250 | 1.25 | 1.85 | 2.65 | 4.9025 | 3.14 | 15.3939 | 0.41336 | 19.55 | 8.0812 | 3.2626 | 2.23 | 7.2755 | 5.3 | 5.67 | 30.051 | 30.7506 | 1.6399 | 8.7129 | 69.5145 | 203.43 | 492 | 12.3 | 285.2445 | 328 | 171 | 169 | 34 | 499 | 497 | 362

## COND CANAL H=2 (hidden)
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [28 empty] | 1
| ADINCIME GENERATOARE SUPERIOARA CONDUCTA Hg = | [7 empty] | 2 | m
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 2.06 | 1.5656 | 3.14 | 4.916 | 0.25833 | 19.55 | 5.0503 | 1.2872 | 2.23 | 2.8704 | 4.12 | 5.67 | 23.3604 | 12.8367 | 0.27842 | 1.4793 | 37.6763 | 9.87 | 757 | 18.925 | 66.4713 | 76.4 | 73 | 72 | 15 | 149.4 | 148.4 | 91.4
| 200 | 0.2 | 0.8 | 2.1 | 1.68 | 3.14 | 5.2752 | 0.29488 | 19.55 | 5.7649 | 1.3537 | 2.23 | 3.0188 | 4.2 | 5.67 | 23.814 | 14.0589 | 0.32628 | 1.7335 | 39.6064 | 11.9 | 757 | 18.925 | 70.4314 | 81 | 82 | 81 | 17 | 163 | 162 | 98
| 250 | 0.25 | 0.85 | 2.15 | 1.8275 | 3.14 | 5.7383 | 0.3408 | 19.55 | 6.6626 | 1.4376 | 2.23 | 3.2059 | 4.3 | 5.67 | 24.381 | 15.6069 | 0.38986 | 2.0713 | 42.0592 | 17 | 757 | 18.925 | 77.9842 | 89.7 | 82 | 81 | 17 | 171.7 | 170.7 | 106.7
| 300 | 0.315 | 0.915 | 2.215 | 2.0267 | 3.14 | 6.3639 | 0.39995 | 19.55 | 7.8191 | 1.5489 | 2.23 | 3.454 | 4.43 | 5.67 | 25.1181 | 17.637 | 0.47785 | 2.5388 | 45.2939 | 24.68 | 757 | 18.925 | 88.8989 | 102.2 | 91 | 90 | 19 | 193.2 | 192.2 | 121.2
| 355 | 0.355 | 0.955 | 2.255 | 2.1535 | 3.14 | 6.7621 | 0.43555 | 19.55 | 8.5149 | 1.619 | 2.23 | 3.6105 | 4.51 | 5.67 | 25.5717 | 18.8875 | 0.53448 | 2.8397 | 47.2989 | 31.35 | 757 | 18.925 | 97.5739 | 112.2 | 91 | 90 | 19 | 203.2 | 202.2 | 131.2
| 400 | 0.4 | 1 | 2.3 | 2.3 | 3.14 | 7.222 | 0.4744 | 19.55 | 9.2745 | 1.7 | 2.23 | 3.791 | 4.6 | 5.67 | 26.082 | 20.2875 | 0.6 | 3.1878 | 49.5573 | 38.44 | 757 | 18.925 | 106.9223 | 123 | 105 | 103 | 22 | 228 | 226 | 145
| 500 | 0.5 | 1.1 | 2.4 | 2.64 | 3.14 | 8.2896 | 0.55412 | 19.55 | 10.8331 | 1.8896 | 2.23 | 4.2139 | 4.8 | 5.67 | 27.216 | 23.3366 | 0.75038 | 3.9867 | 54.5393 | 70.24 | 757 | 18.925 | 143.7043 | 165.3 | 105 | 103 | 22 | 270.3 | 268.3 | 187.3
| 600 | 0.6 | 1.2 | 2.5 | 3 | 3.14 | 9.42 | 0.62088 | 19.55 | 12.1382 | 2.0965 | 2.23 | 4.6752 | 5 | 5.67 | 28.35 | 26.2334 | 0.90348 | 4.8002 | 59.3836 | 87.89 | 757 | 18.925 | 166.1986 | 191.1 | 123 | 121 | 26 | 314.1 | 312.1 | 217.1
| 700 | 0.7 | 1.3 | 2.6 | 3.38 | 3.14 | 10.6132 | 0.66995 | 19.55 | 13.0976 | 2.3254 | 2.23 | 5.1856 | 5.2 | 5.67 | 29.484 | 28.8965 | 1.0546 | 5.6031 | 63.9836 | 114.2 | 989 | 24.725 | 202.9086 | 233.3 | 123 | 121 | 26 | 356.3 | 354.3 | 259.3
| 800 | 0.8 | 1.4 | 2.7 | 3.78 | 3.14 | 11.8692 | 0.69664 | 19.55 | 13.6193 | 2.581 | 2.23 | 5.7555 | 5.4 | 5.67 | 30.618 | 31.2441 | 1.199 | 6.3705 | 68.2326 | 140.9 | 989 | 24.725 | 233.8576 | 268.9 | 145 | 143 | 30 | 413.9 | 411.9 | 298.9
| 900 | 0.9 | 1.5 | 2.8 | 4.2 | 3.14 | 13.188 | 0.69623 | 19.55 | 13.6112 | 2.8679 | 2.23 | 6.3955 | 5.6 | 5.67 | 31.752 | 33.1947 | 1.3321 | 7.0773 | 72.024 | 149 | 989 | 24.725 | 245.749 | 282.6 | 145 | 143 | 30 | 427.6 | 425.6 | 312.6
| 1000 | 1 | 1.6 | 2.9 | 4.64 | 3.14 | 14.5696 | 0.664 | 19.55 | 12.9812 | 3.191 | 2.23 | 7.1159 | 5.8 | 5.67 | 32.886 | 34.6667 | 1.449 | 7.6985 | 75.2513 | 166.5 | 989 | 24.725 | 266.4763 | 306.4 | 171 | 169 | 34 | 477.4 | 475.4 | 340.4
| 1250 | 1.25 | 1.85 | 3.15 | 5.8275 | 3.14 | 18.2983 | 0.41336 | 19.55 | 8.0812 | 4.1876 | 2.23 | 9.3383 | 6.3 | 5.67 | 35.721 | 35.7178 | 1.6399 | 8.7129 | 80.1517 | 203.43 | 989 | 24.725 | 308.3067 | 354.6 | 171 | 169 | 34 | 525.6 | 523.6 | 388.6
0

## COND CANAL H=2.5 (hidden)
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [28 empty] | 1
| ADINCIME GENERATOARE SUPERIOARA CONDUCTA Hg = | [7 empty] | 2.5 | m
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 2.56 | 1.9456 | 3.14 | 6.1092 | 0.25833 | 19.55 | 5.0503 | 1.6672 | 2.23 | 3.7178 | 5.12 | 5.67 | 29.0304 | 14.8773 | 0.27842 | 1.4793 | 45.3869 | 9.87 | 757 | 18.925 | 74.1819 | 85.3 | 73 | 72 | 15 | 158.3 | 157.3 | 100.3
| 200 | 0.2 | 0.8 | 2.6 | 2.08 | 3.14 | 6.5312 | 0.29488 | 19.55 | 5.7649 | 1.7537 | 2.23 | 3.9108 | 5.2 | 5.67 | 29.484 | 16.2069 | 0.32628 | 1.7335 | 47.4244 | 11.9 | 757 | 18.925 | 78.2494 | 90 | 82 | 81 | 17 | 172 | 171 | 107
| 250 | 0.25 | 0.85 | 2.65 | 2.2525 | 3.14 | 7.0728 | 0.3408 | 19.55 | 6.6626 | 1.8626 | 2.23 | 4.1537 | 5.3 | 5.67 | 30.051 | 17.8891 | 0.38986 | 2.0713 | 50.0114 | 17 | 757 | 18.925 | 85.9364 | 98.8 | 82 | 81 | 17 | 180.8 | 179.8 | 115.8
| 300 | 0.315 | 0.915 | 2.715 | 2.4842 | 3.14 | 7.8005 | 0.39995 | 19.55 | 7.8191 | 2.0064 | 2.23 | 4.4742 | 5.43 | 5.67 | 30.7881 | 20.0938 | 0.47785 | 2.5388 | 53.4207 | 24.68 | 757 | 18.925 | 97.0257 | 111.6 | 91 | 90 | 19 | 202.6 | 201.6 | 130.6
| 355 | 0.355 | 0.955 | 2.755 | 2.631 | 3.14 | 8.2614 | 0.43555 | 19.55 | 8.5149 | 2.0965 | 2.23 | 4.6753 | 5.51 | 5.67 | 31.2417 | 21.4517 | 0.53448 | 2.8397 | 55.533 | 31.35 | 757 | 18.925 | 105.808 | 121.7 | 91 | 90 | 19 | 212.7 | 211.7 | 140.7
| 400 | 0.4 | 1 | 2.8 | 2.8 | 3.14 | 8.792 | 0.4744 | 19.55 | 9.2745 | 2.2 | 2.23 | 4.906 | 5.6 | 5.67 | 31.752 | 22.9725 | 0.6 | 3.1878 | 57.9123 | 38.44 | 757 | 18.925 | 115.2773 | 132.6 | 105 | 103 | 22 | 237.6 | 235.6 | 154.6
| 500 | 0.5 | 1.1 | 2.9 | 3.19 | 3.14 | 10.0166 | 0.55412 | 19.55 | 10.8331 | 2.4396 | 2.23 | 5.4404 | 5.8 | 5.67 | 32.886 | 26.2901 | 0.75038 | 3.9867 | 63.1628 | 70.24 | 757 | 18.925 | 152.3278 | 175.2 | 105 | 103 | 22 | 280.2 | 278.2 | 197.2
| 600 | 0.6 | 1.2 | 3 | 3.6 | 3.14 | 11.304 | 0.62088 | 19.55 | 12.1382 | 2.6965 | 2.23 | 6.0132 | 6 | 5.67 | 34.02 | 29.4554 | 0.90348 | 4.8002 | 68.2756 | 87.89 | 757 | 18.925 | 175.0906 | 201.4 | 123 | 121 | 26 | 324.4 | 322.4 | 227.4
| 700 | 0.7 | 1.3 | 3.1 | 4.03 | 3.14 | 12.6542 | 0.66995 | 19.55 | 13.0976 | 2.9754 | 2.23 | 6.6351 | 6.2 | 5.67 | 35.154 | 32.387 | 1.0546 | 5.6031 | 73.1441 | 114.2 | 989 | 24.725 | 212.0691 | 243.9 | 123 | 121 | 26 | 366.9 | 364.9 | 269.9
| 800 | 0.8 | 1.4 | 3.2 | 4.48 | 3.14 | 14.0672 | 0.69664 | 19.55 | 13.6193 | 3.281 | 2.23 | 7.3165 | 6.4 | 5.67 | 36.288 | 35.0031 | 1.199 | 6.3705 | 77.6616 | 140.9 | 989 | 24.725 | 243.2866 | 279.8 | 145 | 143 | 30 | 424.8 | 422.8 | 309.8
| 900 | 0.9 | 1.5 | 3.3 | 4.95 | 3.14 | 15.543 | 0.69623 | 19.55 | 13.6112 | 3.6179 | 2.23 | 8.068 | 6.6 | 5.67 | 37.422 | 37.2222 | 1.3321 | 7.0773 | 81.7215 | 149 | 989 | 24.725 | 255.4465 | 293.7 | 145 | 143 | 30 | 438.7 | 436.7 | 323.7
| 1000 | 1 | 1.6 | 3.4 | 5.44 | 3.14 | 17.0816 | 0.664 | 19.55 | 12.9812 | 3.991 | 2.23 | 8.8999 | 6.8 | 5.67 | 38.556 | 38.9627 | 1.449 | 7.6985 | 85.2173 | 166.5 | 989 | 24.725 | 276.4423 | 317.9 | 171 | 169 | 34 | 488.9 | 486.9 | 351.9
| 1250 | 1.25 | 1.85 | 3.65 | 6.7525 | 3.14 | 21.2029 | 0.41336 | 19.55 | 8.0812 | 5.1126 | 2.23 | 11.401 | 7.3 | 5.67 | 41.391 | 40.6851 | 1.6399 | 8.7129 | 90.789 | 203.43 | 989 | 24.725 | 318.944 | 366.8 | 171 | 169 | 34 | 537.8 | 535.8 | 400.8

## COND CANAL H=3 (hidden)
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [28 empty] | 1
| ADINCIME GENERATOARE SUPERIOARA CONDUCTA Hg = | [7 empty] | 3 | m
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 3.06 | 2.3256 | 3.14 | 7.3024 | 0.25833 | 19.55 | 5.0503 | 2.0472 | 2.23 | 4.5652 | 6.12 | 5.67 | 34.7004 | 16.9179 | 0.27842 | 1.4793 | 53.0975 | 9.87 | 757 | 18.925 | 81.8925 | 94.2 | 73 | 72 | 15 | 167.2 | 166.2 | 109.2
| 200 | 0.2 | 0.8 | 3.1 | 2.48 | 3.14 | 7.7872 | 0.29488 | 19.55 | 5.7649 | 2.1537 | 2.23 | 4.8028 | 6.2 | 5.67 | 35.154 | 18.3549 | 0.32628 | 1.7335 | 55.2424 | 11.9 | 757 | 18.925 | 86.0674 | 99 | 82 | 81 | 17 | 181 | 180 | 116
| 250 | 0.25 | 0.85 | 3.15 | 2.6775 | 3.14 | 8.4073 | 0.3408 | 19.55 | 6.6626 | 2.2876 | 2.23 | 5.1014 | 6.3 | 5.67 | 35.721 | 20.1714 | 0.38986 | 2.0713 | 57.9637 | 17 | 757 | 18.925 | 93.8887 | 108 | 82 | 81 | 17 | 190 | 189 | 125
| 300 | 0.315 | 0.915 | 3.215 | 2.9417 | 3.14 | 9.237 | 0.39995 | 19.55 | 7.8191 | 2.4639 | 2.23 | 5.4945 | 6.43 | 5.67 | 36.4581 | 22.5506 | 0.47785 | 2.5388 | 61.5475 | 24.68 | 757 | 18.925 | 105.1525 | 120.9 | 91 | 90 | 19 | 211.9 | 210.9 | 139.9
| 355 | 0.355 | 0.955 | 3.255 | 3.1085 | 3.14 | 9.7608 | 0.43555 | 19.55 | 8.5149 | 2.574 | 2.23 | 5.7401 | 6.51 | 5.67 | 36.9117 | 24.0158 | 0.53448 | 2.8397 | 63.7672 | 31.35 | 757 | 18.925 | 114.0422 | 131.1 | 91 | 90 | 19 | 222.1 | 221.1 | 150.1
| 400 | 0.4 | 1 | 3.3 | 3.3 | 3.14 | 10.362 | 0.4744 | 19.55 | 9.2745 | 2.7 | 2.23 | 6.021 | 6.6 | 5.67 | 37.422 | 25.6575 | 0.6 | 3.1878 | 66.2673 | 38.44 | 757 | 18.925 | 123.6323 | 142.2 | 105 | 103 | 22 | 247.2 | 245.2 | 164.2
| 500 | 0.5 | 1.1 | 3.4 | 3.74 | 3.14 | 11.7436 | 0.55412 | 19.55 | 10.8331 | 2.9896 | 2.23 | 6.6669 | 6.8 | 5.67 | 38.556 | 29.2436 | 0.75038 | 3.9867 | 71.7863 | 70.24 | 757 | 18.925 | 160.9513 | 185.1 | 105 | 103 | 22 | 290.1 | 288.1 | 207.1
| 600 | 0.6 | 1.2 | 3.5 | 4.2 | 3.14 | 13.188 | 0.62088 | 19.55 | 12.1382 | 3.2965 | 2.23 | 7.3512 | 7 | 5.67 | 39.69 | 32.6774 | 0.90348 | 4.8002 | 77.1676 | 87.89 | 757 | 18.925 | 183.9826 | 211.6 | 123 | 121 | 26 | 334.6 | 332.6 | 237.6
| 700 | 0.7 | 1.3 | 3.6 | 4.68 | 3.14 | 14.6952 | 0.66995 | 19.55 | 13.0976 | 3.6254 | 2.23 | 8.0846 | 7.2 | 5.67 | 40.824 | 35.8775 | 1.0546 | 5.6031 | 82.3046 | 114.2 | 989 | 24.725 | 221.2296 | 254.4 | 123 | 121 | 26 | 377.4 | 375.4 | 280.4
| 800 | 0.8 | 1.4 | 3.7 | 5.18 | 3.14 | 16.2652 | 0.69664 | 19.55 | 13.6193 | 3.981 | 2.23 | 8.8775 | 7.4 | 5.67 | 41.958 | 38.7621 | 1.199 | 6.3705 | 87.0906 | 140.9 | 989 | 24.725 | 252.7156 | 290.6 | 145 | 143 | 30 | 435.6 | 433.6 | 320.6
| 900 | 0.9 | 1.5 | 3.8 | 5.7 | 3.14 | 17.898 | 0.69623 | 19.55 | 13.6112 | 4.3679 | 2.23 | 9.7405 | 7.6 | 5.67 | 43.092 | 41.2497 | 1.3321 | 7.0773 | 91.419 | 149 | 989 | 24.725 | 265.144 | 304.9 | 145 | 143 | 30 | 449.9 | 447.9 | 334.9
| 1000 | 1 | 1.6 | 3.9 | 6.24 | 3.14 | 19.5936 | 0.664 | 19.55 | 12.9812 | 4.791 | 2.23 | 10.6839 | 7.8 | 5.67 | 44.226 | 43.2587 | 1.449 | 7.6985 | 95.1833 | 166.5 | 989 | 24.725 | 286.4083 | 329.4 | 171 | 169 | 34 | 500.4 | 498.4 | 363.4
| 1250 | 1.25 | 1.85 | 4.15 | 7.6775 | 3.14 | 24.1074 | 0.41336 | 19.55 | 8.0812 | 6.0376 | 2.23 | 13.4638 | 8.3 | 5.67 | 47.061 | 45.6523 | 1.6399 | 8.7129 | 101.4262 | 203.43 | 989 | 24.725 | 329.5812 | 379 | 171 | 169 | 34 | 550 | 548 | 413

## COND CANAL H=4 (hidden)
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [28 empty] | 1
| ADINCIME GENERATOARE SUPERIOARA CONDUCTA Hg = | [7 empty] | 4 | m
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 10% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 4.06 | 3.0856 | 3.14 | 9.6888 | 0.25833 | 19.55 | 5.0503 | 2.8072 | 2.23 | 6.26 | 8.12 | 5.67 | 46.0404 | 20.9991 | 0.27842 | 1.4793 | 68.5187 | 9.87 | 815 | 20.375 | 98.7637 | 108.6 | 73 | 72 | 15 | 181.6 | 180.6 | 123.6
| 200 | 0.2 | 0.8 | 4.1 | 3.28 | 3.14 | 10.2992 | 0.29488 | 19.55 | 5.7649 | 2.9537 | 2.23 | 6.5868 | 8.2 | 5.67 | 46.494 | 22.6509 | 0.32628 | 1.7335 | 70.8784 | 11.9 | 815 | 20.375 | 103.1534 | 113.5 | 82 | 81 | 17 | 195.5 | 194.5 | 130.5
| 250 | 0.25 | 0.85 | 4.15 | 3.5275 | 3.14 | 11.0763 | 0.3408 | 19.55 | 6.6626 | 3.1376 | 2.23 | 6.9969 | 8.3 | 5.67 | 47.061 | 24.7359 | 0.38986 | 2.0713 | 73.8682 | 17 | 815 | 20.375 | 111.2432 | 122.4 | 82 | 81 | 17 | 204.4 | 203.4 | 139.4
| 300 | 0.315 | 0.915 | 4.215 | 3.8567 | 3.14 | 12.1101 | 0.39995 | 19.55 | 7.8191 | 3.3789 | 2.23 | 7.5349 | 8.43 | 5.67 | 47.7981 | 27.4641 | 0.47785 | 2.5388 | 77.801 | 24.68 | 815 | 20.375 | 122.856 | 135.1 | 91 | 90 | 19 | 226.1 | 225.1 | 154.1
| 355 | 0.355 | 0.955 | 4.255 | 4.0635 | 3.14 | 12.7595 | 0.43555 | 19.55 | 8.5149 | 3.529 | 2.23 | 7.8698 | 8.51 | 5.67 | 48.2517 | 29.1442 | 0.53448 | 2.8397 | 80.2356 | 31.35 | 815 | 20.375 | 131.9606 | 145.2 | 91 | 90 | 19 | 236.2 | 235.2 | 164.2
| 400 | 0.4 | 1 | 4.3 | 4.3 | 3.14 | 13.502 | 0.4744 | 19.55 | 9.2745 | 3.7 | 2.23 | 8.251 | 8.6 | 5.67 | 48.762 | 31.0275 | 0.6 | 3.1878 | 82.9773 | 38.44 | 815 | 20.375 | 141.7923 | 156 | 105 | 103 | 22 | 261 | 259 | 178
| 500 | 0.5 | 1.1 | 4.4 | 4.84 | 3.14 | 15.1976 | 0.55412 | 19.55 | 10.8331 | 4.0896 | 2.23 | 9.1199 | 8.8 | 5.67 | 49.896 | 35.1506 | 0.75038 | 3.9867 | 89.0333 | 70.24 | 815 | 20.375 | 179.6483 | 197.6 | 105 | 103 | 22 | 302.6 | 300.6 | 219.6
| 600 | 0.6 | 1.2 | 4.5 | 5.4 | 3.14 | 16.956 | 0.62088 | 19.55 | 12.1382 | 4.4965 | 2.23 | 10.0272 | 9 | 5.67 | 51.03 | 39.1214 | 0.90348 | 4.8002 | 94.9516 | 87.89 | 815 | 20.375 | 203.2166 | 223.5 | 123 | 121 | 26 | 346.5 | 344.5 | 249.5
| 700 | 0.7 | 1.3 | 4.6 | 5.98 | 3.14 | 18.7772 | 0.66995 | 19.55 | 13.0976 | 4.9254 | 2.23 | 10.9836 | 9.2 | 5.67 | 52.164 | 42.8585 | 1.0546 | 5.6031 | 100.6256 | 114.2 | 1047 | 26.175 | 241.0006 | 265.1 | 123 | 121 | 26 | 388.1 | 386.1 | 291.1
| 800 | 0.8 | 1.4 | 4.7 | 6.58 | 3.14 | 20.6612 | 0.69664 | 19.55 | 13.6193 | 5.381 | 2.23 | 11.9995 | 9.4 | 5.67 | 53.298 | 46.2801 | 1.199 | 6.3705 | 105.9486 | 140.9 | 1047 | 26.175 | 273.0236 | 300.3 | 145 | 143 | 30 | 445.3 | 443.3 | 330.3
| 900 | 0.9 | 1.5 | 4.8 | 7.2 | 3.14 | 22.608 | 0.69623 | 19.55 | 13.6112 | 5.8679 | 2.23 | 13.0855 | 9.6 | 5.67 | 54.432 | 49.3047 | 1.3321 | 7.0773 | 110.814 | 149 | 1047 | 26.175 | 285.989 | 314.6 | 145 | 143 | 30 | 459.6 | 457.6 | 344.6
| 1000 | 1 | 1.6 | 4.9 | 7.84 | 3.14 | 24.6176 | 0.664 | 19.55 | 12.9812 | 6.391 | 2.23 | 14.2519 | 9.8 | 5.67 | 55.566 | 51.8507 | 1.449 | 7.6985 | 115.1153 | 166.5 | 1047 | 26.175 | 307.7903 | 338.6 | 171 | 169 | 34 | 509.6 | 507.6 | 372.6
| 1250 | 1.25 | 1.85 | 5.15 | 9.5275 | 3.14 | 29.9164 | 0.41336 | 19.55 | 8.0812 | 7.8876 | 2.23 | 17.5893 | 10.3 | 5.67 | 58.401 | 55.5868 | 1.6399 | 8.7129 | 122.7007 | 203.43 | 1047 | 26.175 | 352.3057 | 387.5 | 171 | 169 | 34 | 558.5 | 556.5 | 421.5
0

## COND CANAL H=5 (hidden)
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [28 empty] | 1
| ADINCIME GENERATOARE SUPERIOARA CONDUCTA Hg = | [7 empty] | 5 | m
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 10% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 5.06 | 3.8456 | 3.14 | 12.0752 | 0.25833 | 19.55 | 5.0503 | 3.5672 | 2.23 | 7.9548 | 10.12 | 5.67 | 57.3804 | 25.0803 | 0.27842 | 1.4793 | 83.9399 | 9.87 | 815 | 20.375 | 114.1849 | 125.6034 | 73 | 72 | 15 | 198.6034 | 197.6034 | 140.6034
| 200 | 0.2 | 0.8 | 5.1 | 4.08 | 3.14 | 12.8112 | 0.29488 | 19.55 | 5.7649 | 3.7537 | 2.23 | 8.3708 | 10.2 | 5.67 | 57.834 | 26.9469 | 0.32628 | 1.7335 | 86.5144 | 11.9 | 815 | 20.375 | 118.7894 | 130.6684 | 82 | 81 | 17 | 212.6684 | 211.6684 | 147.6684
| 250 | 0.25 | 0.85 | 5.15 | 4.3775 | 3.14 | 13.7453 | 0.3408 | 19.55 | 6.6626 | 3.9876 | 2.23 | 8.8924 | 10.3 | 5.67 | 58.401 | 29.3004 | 0.38986 | 2.0713 | 89.7727 | 17 | 815 | 20.375 | 127.1477 | 139.9 | 82 | 81 | 17 | 221.9 | 220.9 | 156.9
| 300 | 0.315 | 0.915 | 5.215 | 4.7717 | 3.14 | 14.9832 | 0.39995 | 19.55 | 7.8191 | 4.2939 | 2.23 | 9.5754 | 10.43 | 5.67 | 59.1381 | 32.3777 | 0.47785 | 2.5388 | 94.0546 | 24.68 | 815 | 20.375 | 139.1096 | 153 | 91 | 90 | 19 | 244 | 243 | 172
| 355 | 0.355 | 0.955 | 5.255 | 5.0185 | 3.14 | 15.7582 | 0.43555 | 19.55 | 8.5149 | 4.484 | 2.23 | 9.9994 | 10.51 | 5.67 | 59.5917 | 34.2725 | 0.53448 | 2.8397 | 96.7039 | 31.35 | 815 | 20.375 | 148.4289 | 163.3 | 91 | 90 | 19 | 254.3 | 253.3 | 182.3
| 400 | 0.4 | 1 | 5.3 | 5.3 | 3.14 | 16.642 | 0.4744 | 19.55 | 9.2745 | 4.7 | 2.23 | 10.481 | 10.6 | 5.67 | 60.102 | 36.3975 | 0.6 | 3.1878 | 99.6873 | 38.44 | 815 | 20.375 | 158.5023 | 174.4 | 105 | 103 | 22 | 279.4 | 277.4 | 196.4
| 500 | 0.5 | 1.1 | 5.4 | 5.94 | 3.14 | 18.6516 | 0.55412 | 19.55 | 10.8331 | 5.1896 | 2.23 | 11.5729 | 10.8 | 5.67 | 61.236 | 41.0576 | 0.75038 | 3.9867 | 106.2803 | 70.24 | 815 | 20.375 | 196.8953 | 216.6 | 105 | 103 | 22 | 321.6 | 319.6 | 238.6
| 600 | 0.6 | 1.2 | 5.5 | 6.6 | 3.14 | 20.724 | 0.62088 | 19.55 | 12.1382 | 5.6965 | 2.23 | 12.7032 | 11 | 5.67 | 62.37 | 45.5654 | 0.90348 | 4.8002 | 112.7356 | 87.89 | 815 | 20.375 | 221.0006 | 243.1 | 123 | 121 | 26 | 366.1 | 364.1 | 269.1
| 700 | 0.7 | 1.3 | 5.6 | 7.28 | 3.14 | 22.8592 | 0.66995 | 19.55 | 13.0976 | 6.2254 | 2.23 | 13.8826 | 11.2 | 5.67 | 63.504 | 49.8395 | 1.0546 | 5.6031 | 118.9466 | 114.2 | 1047 | 26.175 | 259.3216 | 285.3 | 123 | 121 | 26 | 408.3 | 406.3 | 311.3
| 800 | 0.8 | 1.4 | 5.7 | 7.98 | 3.14 | 25.0572 | 0.69664 | 19.55 | 13.6193 | 6.781 | 2.23 | 15.1215 | 11.4 | 5.67 | 64.638 | 53.7981 | 1.199 | 6.3705 | 124.8066 | 140.9 | 1047 | 26.175 | 291.8816 | 321.1 | 145 | 143 | 30 | 466.1 | 464.1 | 351.1
| 900 | 0.9 | 1.5 | 5.8 | 8.7 | 3.14 | 27.318 | 0.69623 | 19.55 | 13.6112 | 7.3679 | 2.23 | 16.4305 | 11.6 | 5.67 | 65.772 | 57.3597 | 1.3321 | 7.0773 | 130.209 | 149 | 1047 | 26.175 | 305.384 | 335.9 | 145 | 143 | 30 | 480.9 | 478.9 | 365.9
| 1000 | 1 | 1.6 | 5.9 | 9.44 | 3.14 | 29.6416 | 0.664 | 19.55 | 12.9812 | 7.991 | 2.23 | 17.8199 | 11.8 | 5.67 | 66.906 | 60.4427 | 1.449 | 7.6985 | 135.0473 | 166.5 | 1047 | 26.175 | 327.7223 | 360.5 | 171 | 169 | 34 | 531.5 | 529.5 | 394.5
| 1250 | 1.25 | 1.85 | 6.15 | 11.3775 | 3.14 | 35.7253 | 0.41336 | 19.55 | 8.0812 | 9.7376 | 2.23 | 21.7148 | 12.3 | 5.67 | 69.741 | 65.5213 | 1.6399 | 8.7129 | 143.9752 | 203.43 | 1047 | 26.175 | 373.5802 | 410.9 | 171 | 169 | 34 | 581.9 | 579.9 | 444.9
0

## COND CANAL H=6 (hidden)
RETELE DE CONDUCTE DE CANALIZARE
SAPATURA SI UMPLUTURA LA CONDUCTE DE CANALIZARI
| Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijiniri
|  | procurare conducte, montaj camine vizitare | [28 empty] | 1
| ADINCIME GENERATOARE SUPERIOARA CONDUCTA Hg = | [7 empty] | 6 | m
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA (Euro/m) | VALOARE CAMIN (LA40M) | CAMIN LA 1M | TOTAL GENERAL | Cu 10% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU |  |  |  |  | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs= De+Hg+Hnisip-0.2 | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/M | eur/BUC | eur/M | EUR/ m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 150 | 0.16 | 0.76 | 6.06 | 4.6056 | 3.14 | 14.4616 | 0.25833 | 19.55 | 5.0503 | 4.3272 | 2.23 | 9.6496 | 12.12 | 5.67 | 68.7204 | 29.1615 | 0.27842 | 1.4793 | 99.3611 | 9.87 | 815 | 20.375 | 129.6061 | 142.6 | 73 | 72 | 15 | 215.6 | 214.6 | 157.6
| 200 | 0.2 | 0.8 | 6.1 | 4.88 | 3.14 | 15.3232 | 0.29488 | 19.55 | 5.7649 | 4.5537 | 2.23 | 10.1548 | 12.2 | 5.67 | 69.174 | 31.2429 | 0.32628 | 1.7335 | 102.1504 | 11.9 | 815 | 20.375 | 134.4254 | 147.9 | 82 | 81 | 17 | 229.9 | 228.9 | 164.9
| 250 | 0.25 | 0.85 | 6.15 | 5.2275 | 3.14 | 16.4143 | 0.3408 | 19.55 | 6.6626 | 4.8376 | 2.23 | 10.7879 | 12.3 | 5.67 | 69.741 | 33.8649 | 0.38986 | 2.0713 | 105.6772 | 17 | 815 | 20.375 | 143.0522 | 157.4 | 82 | 81 | 17 | 239.4 | 238.4 | 174.4
| 300 | 0.315 | 0.915 | 6.215 | 5.6867 | 3.14 | 17.8563 | 0.39995 | 19.55 | 7.8191 | 5.2089 | 2.23 | 11.6158 | 12.43 | 5.67 | 70.4781 | 37.2912 | 0.47785 | 2.5388 | 110.3081 | 24.68 | 815 | 20.375 | 155.3631 | 171 | 91 | 90 | 19 | 262 | 261 | 190
| 355 | 0.355 | 0.955 | 6.255 | 5.9735 | 3.14 | 18.7569 | 0.43555 | 19.55 | 8.5149 | 5.439 | 2.23 | 12.1291 | 12.51 | 5.67 | 70.9317 | 39.4009 | 0.53448 | 2.8397 | 113.1723 | 31.35 | 815 | 20.375 | 164.8973 | 181.4 | 91 | 90 | 19 | 272.4 | 271.4 | 200.4
| 400 | 0.4 | 1 | 6.3 | 6.3 | 3.14 | 19.782 | 0.4744 | 19.55 | 9.2745 | 5.7 | 2.23 | 12.711 | 12.6 | 5.67 | 71.442 | 41.7675 | 0.6 | 3.1878 | 116.3973 | 38.44 | 815 | 20.375 | 175.2123 | 192.7 | 105 | 103 | 22 | 297.7 | 295.7 | 214.7
| 500 | 0.5 | 1.1 | 6.4 | 7.04 | 3.14 | 22.1056 | 0.55412 | 19.55 | 10.8331 | 6.2896 | 2.23 | 14.0259 | 12.8 | 5.67 | 72.576 | 46.9646 | 0.75038 | 3.9867 | 123.5273 | 70.24 | 815 | 20.375 | 214.1423 | 235.6 | 105 | 103 | 22 | 340.6 | 338.6 | 257.6
| 600 | 0.6 | 1.2 | 6.5 | 7.8 | 3.14 | 24.492 | 0.62088 | 19.55 | 12.1382 | 6.8965 | 2.23 | 15.3792 | 13 | 5.67 | 73.71 | 52.0094 | 0.90348 | 4.8002 | 130.5196 | 87.89 | 815 | 20.375 | 238.7846 | 262.7 | 123 | 121 | 26 | 385.7 | 383.7 | 288.7
| 700 | 0.7 | 1.3 | 6.6 | 8.58 | 3.14 | 26.9412 | 0.66995 | 19.55 | 13.0976 | 7.5254 | 2.23 | 16.7816 | 13.2 | 5.67 | 74.844 | 56.8205 | 1.0546 | 5.6031 | 137.2676 | 114.2 | 1047 | 26.175 | 277.6426 | 305.4 | 123 | 121 | 26 | 428.4 | 426.4 | 331.4
| 800 | 0.8 | 1.4 | 6.7 | 9.38 | 3.14 | 29.4532 | 0.69664 | 19.55 | 13.6193 | 8.181 | 2.23 | 18.2435 | 13.4 | 5.67 | 75.978 | 61.3161 | 1.199 | 6.3705 | 143.6646 | 140.9 | 1047 | 26.175 | 310.7396 | 341.8 | 145 | 143 | 30 | 486.8 | 484.8 | 371.8
| 900 | 0.9 | 1.5 | 6.8 | 10.2 | 3.14 | 32.028 | 0.69623 | 19.55 | 13.6112 | 8.8679 | 2.23 | 19.7755 | 13.6 | 5.67 | 77.112 | 65.4147 | 1.3321 | 7.0773 | 149.604 | 149 | 1047 | 26.175 | 324.779 | 357.3 | 145 | 143 | 30 | 502.3 | 500.3 | 387.3
| 1000 | 1 | 1.6 | 6.9 | 11.04 | 3.14 | 34.6656 | 0.664 | 19.55 | 12.9812 | 9.591 | 2.23 | 21.3879 | 13.8 | 5.67 | 78.246 | 69.0347 | 1.449 | 7.6985 | 154.9793 | 166.5 | 1047 | 26.175 | 347.6543 | 382.4 | 171 | 169 | 34 | 553.4 | 551.4 | 416.4
| 1250 | 1.25 | 1.85 | 7.15 | 13.2275 | 3.14 | 41.5343 | 0.41336 | 19.55 | 8.0812 | 11.5876 | 2.23 | 25.8403 | 14.3 | 5.67 | 81.081 | 75.4558 | 1.6399 | 8.7129 | 165.2497 | 203.43 | 1047 | 26.175 | 394.8547 | 434.3 | 171 | 169 | 34 | 605.3 | 603.3 | 468.3

## COND REF
Calculatie preturi unitare comasate, manopera , utilaj, transport
PROCURARE SI MONTAJ CONDUCTE REFULARE APA UZATA, PEID PN 10
A. | Cuprinde: | Sapatura, umplutura, pat nisip, umplutura nisip, sprijIniri
|  | procurare si montaj conducta cu elemente de legatura, vane de linie, | [28 empty] | 1
aerisiri si goliri.
| Hg = | 1.2
| DIMENSIUNI |  |  |  | SAPATURA |  |  | UMPLUTURA NISIP ( 0.1m sub cond.) |  |  | UMPLUTURA PAMINT |  |  | SPRIJINIRI |  |  | TOTAL fara sprijiniri (Euro/m) | VOLUM PAMANT EXCEDENTAR | VALOARE TRANSPORT PAMANT EXCEDENTAR | VALOARE TERASAMENTE cu sprijiniri (Euro/m) | MONTAJ CONDUCTA PEID Pn10 | VANE LINIE | CAMIN AERISIRE | CAMIN VANE GOLIRE | TOTAL GENERAL | Cu 15% SF | Desfacere refacere sistem rutier |  |  | TOTAL GENERAL INCLUSIV DESFACERE/REFACERE DRUM
[6 empty] | PU | PU |  | PU | PU |  | PU | PU |  | PU | PU | PU |  | 2.53 euro/t | PU | [5 empty] | PU | PU | PU | PU | PU | PU | PU
| Dn | De (m) | L (m) | Hs* | Vsap (mc) | EUR/ mc | EUR/ m | Vpat nisip (mc) | EUR/ mc | EUR/ m | Vpamint (mc) | EUR/ mc | EUR/ m | Suprafata (mp) | EUR/ mp | EUR/ m | EUR/ m | mc | eur/m | EUR/ m | eur/m | eur/m | eur/m | eur/m | eur/m | EUR/ m | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML | ASFALT EUR/ML | BETON EUR/ML | MACADAM EUR/ML
| 50 | 0.05 | 0.65 | 1.15 | 0.7475 | 3.14 | 2.3472 | 0.096224 | 19.55 | 1.8812 | 0.64931 | 2.23 | 1.448 | 2.3 | 0 | 0 | 5.6763 | 0.098187 | 0.52167 | 6.198 | 5 | - | 1.29 | 0.65 | 13.138 | 15.1 | 64 | 63 | 13 | 79.1 | 78.1 | 28.1 | 50
| 63 | 0.063 | 0.663 | 1.163 | 0.77107 | 3.14 | 2.4212 | 0.106 | 19.55 | 2.0724 | 0.66195 | 2.23 | 1.4761 | 2.326 | 0 | 0 | 5.9697 | 0.10912 | 0.57975 | 6.5494 | 5.97 | - | 1.29 | 0.65 | 14.4594 | 16.6 | 64 | 63 | 13 | 80.6 | 79.6 | 29.6 | 63
| 75 | 0.075 | 0.675 | 1.175 | 0.79312 | 3.14 | 2.4904 | 0.11514 | 19.55 | 2.2511 | 0.67356 | 2.23 | 1.502 | 2.35 | 0 | 0 | 6.2435 | 0.11956 | 0.63522 | 6.8788 | 7.1 | - | 1.31 | 0.66 | 15.9488 | 18.3 | 64 | 63 | 13 | 82.3 | 81.3 | 31.3 | 75
| 90 | 0.09 | 0.69 | 1.19 | 0.8211 | 3.14 | 2.5783 | 0.12671 | 19.55 | 2.4772 | 0.68803 | 2.23 | 1.5343 | 2.38 | 0 | 0 | 6.5898 | 0.13307 | 0.70701 | 7.2968 | 9.74 | 0 | 1.33 | 0.67 | 19.0368 | 21.8923 | 64 | 63 | 13 | 85.8923 | 84.8923 | 34.8923 | 90
| 100 | 0.11 | 0.71 | 1.21 | 0.8591 | 3.14 | 2.6976 | 0.14236 | 19.55 | 2.7831 | 0.70725 | 2.23 | 1.5772 | 2.42 | 0 | 0 | 7.0578 | 0.15185 | 0.8068 | 7.8646 | 13.21 | 0 | 1.35 | 0.68 | 23.1046 | 26.5703 | 73 | 72 | 15 | 99.5703 | 98.5703 | 41.5703 | 110
| 125 | 0.125 | 0.725 | 1.225 | 0.88813 | 3.14 | 2.7887 | 0.15423 | 19.55 | 3.0152 | 0.72163 | 2.23 | 1.6092 | 2.45 | 0 | 0 | 7.4132 | 0.1665 | 0.8846 | 8.2978 | 17.23 | 0 | 1.37 | 0.69 | 27.5878 | 31.726 | 73 | 72 | 15 | 104.726 | 103.726 | 46.726 | 125
| 125 | 0.14 | 0.74 | 1.24 | 0.9176 | 3.14 | 2.8813 | 0.16621 | 19.55 | 3.2495 | 0.736 | 2.23 | 1.6413 | 2.48 | 0 | 0 | 7.772 | 0.1816 | 0.96484 | 8.7369 | 18.75 | 0 | 1.37 | 0.69 | 29.5469 | 33.9789 | 73 | 72 | 15 | 106.9789 | 105.9789 | 48.9789 | 140
| 150 | 0.16 | 0.76 | 1.26 | 0.9576 | 3.14 | 3.0069 | 0.18233 | 19.55 | 3.5645 | 0.75518 | 2.23 | 1.684 | 2.52 | 0 | 0 | 8.2554 | 0.20242 | 1.0755 | 9.3309 | 24.49 | 0 | 1.4 | 0.71 | 35.9309 | 41.3205 | 73 | 72 | 15 | 114.3205 | 113.3205 | 56.3205 | 160
| 150 | 0.18 | 0.78 | 1.28 | 0.9984 | 3.14 | 3.135 | 0.19856 | 19.55 | 3.8819 | 0.7744 | 2.23 | 1.7269 | 2.56 | 0 | 0 | 8.7438 | 0.224 | 1.1901 | 9.9339 | 28.3 | 0 | 1.4 | 0.71 | 40.3439 | 46.3954 | 73 | 72 | 15 | 119.3954 | 118.3954 | 61.3954 | 180
| 200 | 0.2 | 0.8 | 1.3 | 1.04 | 3.14 | 3.2656 | 0.21488 | 19.55 | 4.2009 | 0.79372 | 2.23 | 1.77 | 2.6 | 0 | 0 | 9.2365 | 0.24628 | 1.3085 | 10.545 | 30.92 | 0 | 1.43 | 0.72 | 43.615 | 50.1572 | 82 | 81 | 17 | 132.1572 | 131.1572 | 67.1572 | 200
| 225 | 0.225 | 0.825 | 1.325 | 1.0931 | 3.14 | 3.4324 | 0.23534 | 19.55 | 4.6009 | 0.81805 | 2.23 | 1.8242 | 2.65 | 0 | 0 | 9.8575 | 0.27508 | 1.4615 | 11.319 | 35.66 | 0 | 1.43 | 0.72 | 49.129 | 56.4984 | 82 | 81 | 17 | 138.4984 | 137.4984 | 73.4984 | 225
| 250 | 0.25 | 0.85 | 1.35 | 1.1475 | 3.14 | 3.6031 | 0.2558 | 19.55 | 5.0008 | 0.84264 | 2.23 | 1.8791 | 2.7 | 5.67 | 15.309 | 10.4831 | 0.30486 | 1.6197 | 27.4118 | 45.99 | 0 | 1.48 | 0.75 | 75.6318 | 86.9766 | 82 | 81 | 17 | 168.9766 | 167.9766 | 103.9766 | 250
| 250 | 0.28 | 0.88 | 1.38 | 1.2144 | 3.14 | 3.8132 | 0.28024 | 19.55 | 5.4787 | 0.87261 | 2.23 | 1.9459 | 2.76 | 5.67 | 15.6492 | 11.2379 | 0.34179 | 1.8159 | 28.703 | 54.81 | 0 | 1.48 | 0.75 | 85.743 | 98.6044 | 82 | 81 | 17 | 180.6044 | 179.6044 | 115.6044 | 280
| 300 | 0.315 | 0.915 | 1.415 | 1.2947 | 3.14 | 4.0654 | 0.30845 | 19.55 | 6.0303 | 0.90838 | 2.23 | 2.0257 | 2.83 | 5.67 | 16.0461 | 12.1214 | 0.38635 | 2.0527 | 30.2202 | 69.94 | 0 | 1.51 | 0.77 | 102.4402 | 117.8062 | 91 | 90 | 19 | 208.8062 | 207.8062 | 136.8062 | 315
| 355 | 0.355 | 0.955 | 1.455 | 1.3895 | 3.14 | 4.3631 | 0.34005 | 19.55 | 6.6479 | 0.95055 | 2.23 | 2.1197 | 2.91 | 5.67 | 16.4997 | 13.1308 | 0.43898 | 2.3323 | 31.9627 | 86.39 | 0 | 2.69 | 1.31 | 122.3527 | 140.7056 | 91 | 90 | 19 | 231.7056 | 230.7056 | 159.7056 | 355
| 400 | 0.4 | 1 | 1.5 | 1.5 | 3.14 | 4.71 | 0.3744 | 19.55 | 7.3195 | 1 | 2.23 | 2.23 | 3 | 5.67 | 17.01 | 14.2595 | 0.5 | 2.6565 | 33.926 | 91.96 | 0 | 2.8 | 1.37 | 130.056 | 149.5644 | 105 | 103 | 22 | 254.5644 | 252.5644 | 171.5644 | 400
| 450 | 0.45 | 1.05 | 1.55 | 1.6275 | 3.14 | 5.1104 | 0.41059 | 19.55 | 8.027 | 1.0579 | 2.23 | 2.3592 | 3.1 | 5.67 | 17.577 | 15.4966 | 0.56955 | 3.026 | 36.0996 | 123 | 0 | 2.8 | 1.37 | 163.2696 | 187.7601 | 105 | 103 | 22 | 292.7601 | 290.7601 | 209.7601 | 450
| 500 | 0.5 | 1.1 | 1.6 | 1.76 | 3.14 | 5.5264 | 0.44412 | 19.55 | 8.6826 | 1.1196 | 2.23 | 2.4968 | 3.2 | 5.67 | 18.144 | 16.7058 | 0.64038 | 3.4023 | 38.2521 | 160 | 0 | 3.81 | 1.91 | 203.9721 | 234.5679 | 105 | 103 | 22 | 339.5679 | 337.5679 | 256.5679 | 500
| 550 | 0.55 | 1.15 | 1.65 | 1.8975 | 3.14 | 5.9581 | 0.47442 | 19.55 | 9.2749 | 1.1856 | 2.23 | 2.6439 | 3.3 | 5.67 | 18.711 | 17.877 | 0.71188 | 3.7822 | 40.3702 | 177 | 0 | 3.81 | 1.91 | 223.0902 | 256.5537 | 105 | 103 | 22 | 361.5537 | 359.5537 | 278.5537 | 550
| 600 | 0.6 | 1.2 | 1.7 | 2.04 | 3.14 | 6.4056 | 0.50088 | 19.55 | 9.7922 | 1.2565 | 2.23 | 2.802 | 3.4 | 5.67 | 19.278 | 18.9998 | 0.78348 | 4.1626 | 42.4405 | 185 | 0 | 7.41 | 3.73 | 238.5805 | 274.3675 | 123 | 121 | 26 | 397.3675 | 395.3675 | 300.3675 | 600
| 700 | 0.7 | 1.3 | 1.8 | 2.34 | 3.14 | 7.3476 | 0.53995 | 19.55 | 10.5561 | 1.4154 | 2.23 | 3.1563 | 3.6 | 5.67 | 20.412 | 21.0601 | 0.9246 | 4.9124 | 46.3845 | 210 | 0 | 7.67 | 3.87 | 267.9245 | 308.1131 | 123 | 121 | 26 | 431.1131 | 429.1131 | 334.1131 | 700
| 800 | 0.8 | 1.4 | 1.9 | 2.66 | 3.14 | 8.3524 | 0.55664 | 19.55 | 10.8823 | 1.601 | 2.23 | 3.5701 | 3.8 | 5.67 | 21.546 | 22.8049 | 1.059 | 5.6267 | 49.9775 | 225 | 0 | 8.46 | 4.3 | 287.7375 | 330.8982 | 123 | 121 | 26 | 453.8982 | 451.8982 | 356.8982 | 800
0
H* - diferenta intre cota teren amenajat si cota sapatura

## Reab CIPP lining
Diametru (mm) | Dn 250 | Dn 315 | Dn 400 | Dn 500 | Dn 600
Reabilitare prin procedeul CIPP Lining (euro/m) | 260 | 290 | 350 | 460 | 610

## SPAU (hidden)
SPAU1 - Q=3 l/s, H=20 m, Di=1.8 | C+I | MU | U | TOTAL | Alimentare cu energie electrica | P (kW)
Constructie statie de pompare | 25130 |  |  | 25130 |  | 4
Pompe |  | 1800 | 9040 | 10840
Instalatii electrice |  | 1390 | 6970 | 8360
44330
SPAU2 - Q=5 l/s, H=20 m, Di=1.8 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 26450 |  |  | 26450 |  | 4
Pompe |  | 1800 | 9040 | 10840
Instalatii electrice |  | 1390 | 6970 | 8360
45650
SPAU3 - Q=10 l/s, H=30 m, Di=2.2 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 29090 |  |  | 29090 |  | 17
Pompe |  | 2300 | 12280 | 14580
Instalatii electrice |  | 1460 | 7300 | 8760
52430
SPAU4 - Q=20 l/s, H=30 m, Di=2.2 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 31740 |  |  | 31740 |  | 17
Pompe |  | 2200 | 12780 | 14980
Instalatii electrice |  | 1770 | 8900 | 10670
57390
SPAU5 - Q=30 l/s, H=30 m, Di=2.2 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 34390 |  |  | 34390 |  | 17
Pompe |  | 2430 | 16180 | 18610
Instalatii electrice |  | 1770 | 8900 | 10670
63670
SPAU6 - Q=45 l/s, H=30 m, Di=3 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 47600 |  |  | 47600 |  | 22
Pompe |  | 2500 | 20810 | 23310
Instalatii electrice |  | 1770 | 8900 | 10670
81580
SPAU7 - Q=60 l/s, H=30 m, Di=3 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 52900 |  |  | 52900 |  | 30
Pompe |  | 2900 | 24150 | 27050
Instalatii electrice |  | 2100 | 10500 | 12600
92550
SPAU8 - Q=80 l/s, H=30 m, Di=3 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 55500 |  |  | 55500 |  | 45
Pompe |  | 3220 | 32340 | 35560
Instalatii electrice |  | 3100 | 15500 | 18600
109660
SPAU9 - Q=100 l/s, H=30 m, Di=3 | C+I | MU | U | TOTAL | Alimentare cu energie electrica
Constructie statie de pompare | 59500 |  |  | 59500 |  | 50
Pompe |  | 4900 | 48900 | 53800
Instalatii electrice |  | 3100 | 15500 | 18600
131900
SPAU9 - Q=150 l/s, H=30 m, Di=3 | C+I | MU | U | TOTAL | Alimentare cu energie electrica |  | SEAU RASTU NOU
Constructie statie de pompare | 70100 |  |  | 70100
Pompe |  | 6400 | 59500 | 65900
Instalatii electrice |  | 3900 | 18500 | 22400
158400

## SPAU_DB
POIM DAMBOVITA - SPAU-uri
[13 empty] | 60% | 10% | 30%
Nr. crt. | Statie de pompare apa uzata | Debit cerut | Debit ofertat | Inaltime de pompare solicitat | Inaltime de pompare ofertat | H radier cond. intrare SPAU | Nr. pompe | Putere nominala/ pompa | Randament | D interior SPAU | H SPAU | Tip Pompe | C + I | MU | U | Pret (fara TVA) | Observatii | D interior Camin Decantor | H Camin Decantor | Pret camin decantor fara TVA | Pret total (fara TVA)
|  | (l/s) | (l/s) | (mCA) | (mCA) | (m) | (buc) | KW | (%) | (m) | (m) |  | (EUR) | (EUR) | (EUR) | (EUR) |  | (m) | (m) | (EUR) | (EUR)
1 | SPAU1 | 3 | 3.2 | 3 | 3.3 | 2 | 1+1 | 1.2 | 26.7 | 1.5 | 3 | Rexa PRO V05 DA-122 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 | Include Tabloul de Automatizare si Control | 1,5 | 2.75 | 0 | 51436
2 | SPAU2 | (l/s): 3; (mCA): 3; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 30861.6 | 5143.6 | 15430.8 | 51436 |  |  |  | 0 | 51436
3 | SPAU3 | 3 | 3.2 | 3 | 3.3 | 3 | 1+1 | 1.2 | 26.7 | 1.5 | 4 | Rexa PRO V05 DA-122 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 3.75 | 0 | 51436
4 | SPAU4 | 3 | 3.2 | 4 | 4.6 | 2.5 | 1+1 | 1.25 | 32.2 | 1.5 | 3.5 | Rexa PRO V06 DA-622 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 3.25 | 0 | 51436
5 | SPAU5 | (l/s): 3; (mCA): 5; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 30861.6 | 5143.6 | 15430.8 | 51436 |  |  |  | 0 | 51436
6 | SPAU6 | 3 | 3.4 | 5 | 6.3 | 3 | 1+1 | 1.2 | 34.6 | 1.5 | 4 | Rexa PRO V05 DA-124 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 3.75 | 0 | 51436
7 | SPAU7 | 3 | 3.4 | 5 | 6.3 | 3.5 | 1+1 | 1.2 | 34.6 | 1.5 | 4 | Rexa PRO V05 DA-124 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 4.25 | 0 | 51436
8 | SPAU8 | (l/s): 3; (mCA): 6; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 30861.6 | 5143.6 | 15430.8 | 51436 |  |  |  | 0 | 51436
9 | SPAU9 | 3 | 3.3 | 6 | 7.3 | 3 | 1+1 | 1.2 | 41 | 1.5 | 4 | Rexa PRO C05 DA-322 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 3.75 | 0 | 51436
10 | SPAU10 | (l/s): 3; (mCA): 7; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 30861.6 | 5143.6 | 15430.8 | 51436 |  |  |  | 0 | 51436
11 | SPAU11 | 3 | 3.1 | 7 | 7.5 | 3 | 1+1 | 1.2 | 40.2 | 1.5 | 4 | Rexa PRO C05 DA-322 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 3.75 | 0 | 51436
12 | SPAU12 | 3 | 3.1 | 7 | 7.5 | 3.5 | 1+1 | 1.2 | 40.2 | 1.5 | 4.5 | Rexa PRO C05 DA-322 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 4.25 | 0 | 51436
13 | SPAU13 | (l/s): 3; (mCA): 8; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
14 | SPAU14 | 3 | 3.4 | 8 | 10 | 3 | 1+1 | 1.2 | 37.6 | 1.5 | 4 | Rexa PRO V05 DA-126 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 3.75 | 0 | 52300
15 | SPAU15 | (l/s): 3; (mCA): 8; (m): 3.5; (buc): 1+1; KW: 1.2 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
16 | SPAU16 | 3 | 3.4 | 8 | 10 | 4 | 1+1 | 1.2 | 37.6 | 1.5 | 5 | Rexa PRO V05 DA-126 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 4.75 | 0 | 52300
17 | SPAU17 | 3 | 3.4 | 8 | 10 | 5 | 1+1 | 1.2 | 37.6 | 1.5 | 6 | Rexa PRO V05 DA-126 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 5.75 | 0 | 52300
18 | SPAU18 | (l/s): 3; (mCA): 9; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
19 | SPAU19 | 3 | 3.2 | 9 | 10.2 | 3 | 1+1 | 1.2 | 36.8 | 1.5 | 4 | Rexa PRO V05 DA-126 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 3.75 | 0 | 52300
20 | SPAU20 | 3 | 3.2 | 9 | 10.2 | 4 | 1+1 | 1.2 | 36.8 | 1.5 | 5 | Rexa PRO V05 DA-126 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 4.75 | 0 | 52300
21 | SPAU21 | (l/s): 3; (mCA): 10; (m): 2; (buc): 1+1; KW: 1.2 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
22 | SPAU22 | (l/s): 3; (mCA): 10; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
23 | SPAU23 | 3 | 3.2 | 10 | 10.2 | 3 | 1+1 | 1.2 | 36.8 | 1.5 | 4 | Rexa PRO V05 DA-126 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 3.75 | 0 | 52300
24 | SPAU24 | 3 | 3.2 | 10 | 11.5 | 3.5 | 1+1 | 1.2 | 44 | 1.5 | 4.5 | Rexa PRO C05 DA-324 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 4.25 | 0 | 52300
25 | SPAU25 | (l/s): 3; (mCA): 11; (m): 2.5; (buc): 1+1; KW: 1.2 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
26 | SPAU26 | 3 | 3.2 | 11 | 11.5 | 3 | 1+1 | 1.2 | 44 | 1.5 | 4 | Rexa PRO C05 DA-324 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 3.75 | 0 | 52300
27 | SPAU27 | (l/s): 3; (mCA): 11; (m): 3.5; (buc): 1+1 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
28 | SPAU28 | 3 | 3.2 | 11 | 11.5 | 4 | 1+1 | 1.2 | 44 | 1.5 | 5 | Rexa PRO C05 DA-324 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 4.75 | 0 | 52300
29 | SPAU29 | 3 | 3.4 | 12 | 15.5 | 2 | 1+1 | 1.65 | 48.1 | 1.5 | 3 | Rexa PRO C05 DA-326 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 2.75 | 0 | 52300
30 | SPAU30 | 3 | 3.4 | 13 | 15.5 | 2 | 1+1 | 1.65 | 48.1 | 1.5 | 3 | Rexa PRO C05 DA-326 / EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 2.75 | 0 | 52300
31 | SPAU31 | 3 | 3.2 | 14 | 15.8 | 2 | 1+1 | 1.65 | 46.5 | 2 | 3.5 | Rexa PRO C05 DA-326/ EA | 31380 | 5230 | 15690 | 52300 |  | 1,5 | 3.95 | 0 | 52300
32 | SPAU32 | 3 | 3.1 | 21 | 22 | 2 | 1+1 | 3.9 | 35.1 | 2 | 3.5 | Rexa PRO V05 DA-226 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 3.85 | 0 | 52700
33 | SPAU33 | 3 | 3 | 25 | 25.2 | 2.5 | 1+1 | 3.9 | 34 | 2 | 4 | Rexa PRO V05 DA-228 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 3.75 | 0 | 52700
34 | SPAU34 | 3.5 | 3.7 | 6 | 6.9 | 3.15 | 1+1 | 1.2 | 42.2 | 2 | 4.65 | Rexa PRO C05 DA-322 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 4.45 | 0 | 52700
35 | SPAU35 | 3.5 | 3.7 | 10 | 11 | 2.5 | 1+1 | 1.2 | 46.1 | 2 | 4 | Rexa PRO C05 DA-324 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 4.45 | 0 | 52700
36 | SPAU36 | 3.5 | 3.7 | 12 | 13.6 | 2.1 | 1+1 | 2.5 | 40.5 | 2 | 3.6 | Rexa PRO V05 DA-222 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 4.45 | 0 | 52700
37 | SPAU37 | 3.5 | 3.5 | 15 | 15.4 | 2.2 | 1+1 | 1.65 | 48.9 | 2 | 3.7 | Rexa PRO C05 DA-326 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 4.25 | 0 | 52700
38 | SPAU38 | 3.5 | 3.5 | 15 | 15.4 | 3.2 | 1+1 | 1.65 | 48.9 | 2 | 4.7 | Rexa PRO C05 DA-326 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 4.25 | 0 | 52700
39 | SPAU39 | 3.5 | 3.5 | 20 | 19.9 | 2.4 | 1+1 | 2.5 | 45.4 | 2 | 3.9 | Rexa PRO C05 DA-328 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 4.25 | 0 | 52700
40 | SPAU40 | 4 | 4.2 | 4 | 4.4 | 3.2 | 1+1 | 1.25 | 35.6 | 2 | 4.7 | Rexa PRO V06 DA-622 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 4.95 | 0 | 51436
41 | SPAU41 | 4.1 | 4.2 | 6 | 6.4 | 2 | 1+1 | 1.2 | 42.9 | 2 | 3.5 | Rexa PRO C05 DA-322 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 4.95 | 0 | 51436
42 | SPAU42 | 4.19 | 4.6 | 7 | 8.6 | 2.9 | 1+1 | 1.2 | 41 | 2 | 4.4 | Rexa PRO V05 DA-126 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 5.35 | 0 | 51436
43 | SPAU43 | 4.5 | 4.5 | 15 | 15.2 | 2.27 | 1+1 | 2.5 | 41.3 | 2 | 3.77 | Rexa PRO V05 DA-224 / EA | 31620 | 5270 | 15810 | 52700 |  | 1,5 | 5.25 | 0 | 52700
44 | SPAU44 | 4.5 | 4.6 | 20 | 21 | 3.05 | 1+1 | 2.5 | 52.7 | 2 | 4.55 | Rexa PRO C05 DA-329 / EA | 32340 | 5390 | 16170 | 53900 |  | 1,5 | 5.35 | 0 | 53900
45 | SPAU45 | 4.8 | 5.4 | 7 | 8.9 | 2.32 | 1+1 | 1.2 | 49.2 | 2 | 3.82 | Rexa PRO C05 DA-324 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 6.15 | 0 | 51436
46 | SPAU46 | 5.42 | 5.6 | 12 | 12.9 | 2.48 | 1+1 | 1.65 | 56.2 | 2 | 3.98 | Rexa PRO C05 DA-326 / EA | 32340 | 5390 | 16170 | 53900 |  | 1,5 | 6.35 | 0 | 53900
47 | SPAU47 | 5.6 | 6 | 7 | 8.2 | 2.28 | 1+1 | 1.2 | 48.9 | 2 | 3.78 | Rexa PRO C05 DA-324 / EA | 30861.6 | 5143.6 | 15430.8 | 51436 |  | 1,5 | 6.75 | 0 | 51436
48 | SPAU48 | 6.55 | 6.8 | 17 | 18.1 | 2 | 1+1 | 2.5 | 58.7 | 2 | 3.5 | Rexa PRO C05 DA-329 / EA | 32340 | 5390 | 16170 | 53900 |  | 1,5 | 7.55 | 0 | 53900
49 | SPAU49 | 6.57 | 6.7 | 30 | 31.6 | 1.65 | 1+1 | 11.5 | 30.9 | 2 | 3.15 | FA 08.73W FK 202-2/17 | 32340 | 5390 | 16170 | 53900 |  | 1,5 | 7.45 | 0 | 53900
50 | SPAU50 | 6.85 | 7 | 23 | 23.9 | 2 | 1+1 | 6.6 | 43 | 2 | 3.5 | FA 08.64E FK 17.1-4/16K | 32340 | 5390 | 16170 | 53900 |  | 1,5 | 7.75 | 0 | 53900
51 | SPAU51 | 8.35 | 8.4 | 14 | 14.1 | 2.58 | 1+1 | 4 | 57 | 2 | 4.28 | FA 10.33E FK 17.1-4/8K | 32502 | 5417 | 16251 | 54170 |  | 1,5 | 9.15 | 0 | 54170
52 | SPAU52 | 9.81 | 9.9 | 13 | 13.1 | 1.65 | 1+1 | 3.9 | 45.8 | 2 | 3.35 | Rexa PRO V06 DA-222 / EA | 32502 | 5417 | 16251 | 54170 |  | 1,5 | 10.65 | 0 | 54170
53 | SPAU53 | 10.01 | 10.2 | 7 | 7.3 | 2.5 | 1+1 | 3.1 | 62.9 | 2 | 4.2 | FA 08.64E FK 17.1-6/12K | 32502 | 5417 | 16251 | 54170 |  | 1,5 | 10.95 | 0 | 54170
54 | SPAU54 | 10.48 | 10.7 | 15 | 15.6 | 2.05 | 1+1 | 5 | 60.7 | 2 | 3.75 | FA 10.33E FK 17.1-4/12K | 33180 | 5530 | 16590 | 55300 |  | 1,5 | 11.45 | 0 | 54170
55 | SPAU55 | 11.89 | 12.2 | 12 | 12.4 | 3.36 | 1+1 | 5 | 65.5 | 2 | 5.06 | FA 10.33E FK 17.1-4/12K | 33180 | 5530 | 16590 | 55300 |  | 1,5 | 12.95 | 0 | 54170
56 | SPAU56 | 13 | 13 | 44 | 44.2 | 2.8 | 1+1 | 17 | 37.8 | 2 | 4.5 | FA 08.73W FK 202-2/22 | 44628 | 7438 | 22314 | 74380 |  | 1,5 | 13.75 | 0 | 74380
57 | SPAU57 | 13.81 | 14.2 | 8 | 8.5 | 2.53 | 1+1 | 3.1 | 68.3 | 2 | 4.23 | FA 10.34E FK 17.1-6/12K | 33180 | 5530 | 16590 | 55300 |  | 1,5 | 14.95 | 0 | 55300
58 | SPAU58 | 14 | 14.4 | 15 | 15.9 | 4.2 | 1+1 | 5 | 66.1 | 2 | 5.9 | FA 10.33E FK 17.1-4/12K | 37500 | 6250 | 18750 | 62500 |  | 1,5 | 15.15 | 0 | 62500
59 | SPAU59 | 15.03 | 16.7 | 10 | 10.9 | 3.62 | 1+1 | 5 | 69.8 | 2 | 5.32 | FA 10.33E FK 17.1-4/12K | 37500 | 6250 | 18750 | 62500 |  | 1,5 | 17.45 | 0 | 62500
60 | SPAU60 | 15.98 | 16.7 | 9 | 10.9 | 3 | 1+1 | 5 | 69.8 | 2 | 4.7 | FA 10.33E FK 17.1-4/12K | 33180 | 5530 | 16590 | 55300 |  | 1,5 | 17.45 | 0 | 55300
61 | SPAU61 | 16.91 | 17.6 | 6 | 6.4 | 2.88 | 1+1 | 4 | 66.8 | 2 | 4.58 | FA 10.51E FK 17.1-4/8K | 33180 | 5530 | 16590 | 55300 |  | 1,5 | 18.35 | 0 | 55300
62 | SPAU62 | 17.31 | 17.4 | 38 | 38.3 | 3.82 | 1+1 | 17 | 43.2 | 2 | 5.52 | FA 08.73W FK 202-2/22 | 44628 | 7438 | 22314 | 74380 |  | 1,5 | 18.15 | 0 | 74380
63 | SPAU63 | 17.93 | 18.4 | 12 | 12.6 | 1.88 | 1+1 | 5 | 71.6 | 2 | 3.58 | FA 10.33E FK 17.1-4/12K | 37500 | 6250 | 18750 | 62500 |  | 1,5 | 19.15 | 0 | 62500
64 | SPAU64 | 18.04 | 18.4 | 12 | 12.6 | 3.53 | 1+1 | 5 | 71.6 | 2 | 5.23 | FA 10.33E FK 17.1-4/12K | 37500 | 6250 | 18750 | 62500 |  | 1,5 | 19.15 | 0 | 62500
65 | SPAU65 | 18.86 | 19.9 | 14 | 15.3 | 3.06 | 1+1 | 6.6 | 72 | 2 | 4.76 | FA 10.33E FK 17.1-4/16K | 37500 | 6250 | 18750 | 62500 |  | 1,5 | 20.65 | 0 | 62500
66 | SPAU66 | 21 | 21 | 15 | 15 | 2.7 | 1+1 | 6.6 | 67.2 | 2 | 4.4 | FA 10.34E FK 17.1-4/16K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 21.75 | 8100 | 80600
67 | SPAU67 | 22 | 22.4 | 13 | 13.5 | 4.5 | 1+1 | 6.6 | 67 | 2 | 6.2 | FA 10.34E FK 17.1-4/16K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 23.15 | 8100 | 80600
68 | SPAU68 | 22.54 | 23 | 40 | 41.7 | 2.88 | 1+1 | 26 | 55.6 | 2.5 | 5.08 | FA 10.78Z FKT 27.1-4/22K | 59880 | 8630 | 25890 | 86300 |  | 1,5 | 23.75 | 8100 | 94400
69 | SPAU69 | 23.5 | 24.1 | 13 | 13.7 | 1.67 | 1+1 | 6.6 | 67.3 | 2 | 3.37 | FA 10.34E FK 17.1-4/16K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 24.85 | 8100 | 80600
70 | SPAU70 | 26.34 | 26.9 | 7 | 7.3 | 2.14 | 1+1 | 4 | 72.9 | 2.5 | 4.34 | FA 10.51E FK 17.1-4/8K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 27.65 | 8100 | 80600
71 | SPAU71 | 27.1 | 27.7 | 13 | 13.5 | 2.55 | 1+1 | 6.6 | 74.9 | 2.5 | 4.75 | FA 10.33E FK 17.1-4/16K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 28.45 | 8100 | 80600
72 | SPAU72 | 27.31 | 28.5 | 10.9 | 10.9 | 2.01 | 1+1 | 6.6 | 66.1 | 2 | 3.71 | FA 10.34E FK 17.1-4/16K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 2.76 | 8100 | 80600
73 | SPAU73 | 29.6 | 29.6 | 20 | 20 | 1.59 | 1+1 | 15 | 70.5 | 2.5 | 3.29 | FA 10.34E FK 202-4/22 | 59880 | 8630 | 25890 | 86300 |  | 1,5 | 2.34 | 8100 | 94400
74 | SPAU74 | 31.91 | 32.1 | 10.1 | 10.1 | 3.28 | 1+1 | 6.6 | 64.5 | 2.5 | 4.98 | FA 10.34E FK 17.1-4/16K | 56820 | 8120 | 24360 | 81200 |  | 1,5 | 4.03 | 8100 | 89300
75 | SPAU75 | 32.59 | 32.7 | 13.1 | 13.1 | 1.7 | 1+1 | 7.8 | 67.1 | 2.5 | 3.4 | FA 10.34E FK 202-4/12 | 56820 | 8120 | 24360 | 81200 |  | 1,5 | 2.45 | 8100 | 89300
76 | SPAU76 | 20 | 20.8 | 15.1 | 15.1 |  | 1+1 | 6.6 | 67.1 | 2 | 1.7 | FA 10.34E FK 17.1-4/16K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 0.75 | 8100 | 80600
77 | SPAU77 | 20.9 | 22.2 | 12.5 | 12.5 |  | 1+1 | 6.6 | 66.8 | 2 | 1.7 | FA 10.34E FK 17.1-4/16K | 51600 | 7250 | 21750 | 72500 |  | 1,5 | 0.75 | 8100 | 80600
78 | SPAU78 | 89 | 89.4 | 11.1 | 11.1 | 4 | 1+1 | 18.5 | 55.4 | 3 | 5.7 | FA 15.95E FK 202-4/27 | 63480 | 9230 | 27690 | 92300 |  | 1,5 | 4.75 | 8100 | 100400
79 | SPAU79 | 89 | 89.7 | 28.5 | 28.5 | 3.62 | 1+1 | 46 | 71.1 | 3 | 5.32 | FA 15.77Z FK 34.1-4/24 | 63480 | 9230 | 27690 | 92300 |  | 1,5 | 4.37 | 8100 | 100400
80 | SPAU80 | 97 | 97.5 | 38.4 | 38.4 | 2.41 | 1+1 | 65 | 70.7 | 3 | 4.11 | FA 15.77Z FK 34.1-4/33 | 77160 | 11510 | 34530 | 115100 |  | 1,5 | 3.16 | 8100 | 123200
81 | SPAU81 | (l/s): 7.6; (l/s): 17; (mCA): 2.1 |  | 30861.6 | 5143.6 | 15430.8 | 51436 |  |  |  | 0 | 51436
82 | SPAU82 | (l/s): 10.2; (l/s): 6; (mCA): 3 |  | 32502 | 5417 | 16251 | 54170 |  |  |  | 0 | 54170
83 | SPAU83 | (l/s): 3; (l/s): 16; (mCA): 16 |  | 31620 | 5270 | 15810 | 52700 |  |  |  | 0 | 52700
84 | SPAU84 | (l/s): 37.18; (l/s): 31; (mCA): 31 |  | 59880 | 8630 | 25890 | 86300 |  |  |  | 8100 | 94400
85 | SPAU85 | (l/s): 3; (l/s): 15; (mCA): 15 |  | 31380 | 5230 | 15690 | 52300 |  |  |  | 0 | 52300
86 | SPAU86 | (l/s): 3; (l/s): 11; (mCA): 11 |  | 31620 | 5270 | 15810 | 52700 |  |  |  | 0 | 52700
87 | SPAU87 | (l/s): 3; (l/s): 17; (mCA): 17 |  | 31620 | 5270 | 15810 | 52700 |  |  |  | 0 | 52700
88 | SPAU88 | (l/s): 40.28; (l/s): 21; (mCA): 21 |  | 59880 | 8630 | 25890 | 86300 |  |  |  | 8100 | 94400
89 | SPAU89 | (l/s): 63.06; (l/s): 18; (mCA): 18 |  | 70412.4 | 10385.4 | 31156.2 | 103854 |  |  |  | 8100 | 111954
90 | SPAU90 | (l/s): 64.4; (l/s): 39; (mCA): 39 |  | 74955 | 11142.5 | 33427.5 | 111425 |  |  |  | 8100 | 119525

## Racord
RACORD DE CANALIZARE PE CONDUCTA D 250 CU 160 (L=10m) SI CAMIN RACORD D1000/H=1m
1
De1/De2 | TOTAL INSTALATII | TERASAMENTE ( 10m conducta bransament) |  | CAMIN DE RACORD CU D1000/H=1m | TOTAL | TOTAL CU COEFICIENT SF 15%
mm
| EURO/BUC | EURO/M | EURO | EURO | EURO | EURO
250/160 | 80 | 8.755 | 87.55 | 280 | 447.55 | 514.7 | racord nou
| 80 | 8.755 | 87.55 | 0 | 167.55 | 192.7 | racord partial fara camin
| 80 | 0 | 0 | 0 | 80 | 92 | refacere racord (reracordare)

## Subtraversari
| Diametre teava PEHD | DN50 | DN63-90 | DN110-140 | DN160-200 | DN225-280 | DN315-355 | DN400-450 | DN500 | DN560-630 | DN800 | DN1200 | De+100
Subtraversari | Diam cond protectie OL | 150 | 200 | 250 | 300 | 400 | 500 | 600 | 700 | 800 | 1000 | 1400
| Pret/m | 165 | 195 | 255 | 300 | 435 | 580.545 | 767.85 | 985.155 | 1181.57 | 1615.75 | 2376
Supratraversare | Diam cond protectie OL | 150 | 200 | 250 | 300 | 400 | 450 | 500 | 600 | 700 | 800 | 1000
| Pret/m |  | 1040 | 1040 | 1040 | 1200 | 1200 |  |  |  |  | 1615.75
Pentru supratraversari independente, cu deschideri mai mari de 15 m se considera: |  |  |  |  | 1630 | Euro/ml

## Generator
1
EUR
Tip generator | EUR/buc
Grup electrogen | 14500
Generator mobil pt SPAU | 5000
Generator fix STAP | …
Generator fix SEAU | …

## Volume de apa
Aglomerare/sistem | Debite (l/s) | Volume anuale (mc/an)
Branesti | 4.99 | 157364.64
TOTAL pt optiunea 1 | 4.99 | 157364.64
TOTAL pt optiunea 2 | 4.99 | 157364.64
TOTAL pt optiunea 3
TOTAL pt optiunea 4
etc
Note on D3: Maria Popescu: la aceste valori se vor raporta costurile de operare CU LINK
Note on C4: Ruxandra Savin: - de inlocuit cu debitul de la Belin!!!

## Personal exploatare
PERSONAL EXPLOATARE
| Optiunea 1 Varianta descentralizata | Personal exploatare-intretinere Statie de epurare | Personal exploatare-intretinere retele de canalizare
| Aglomerarea Belin | 3 | 0
| TOTAL | 3 | 0
| TOTAL GENERAL | 3
| Optiunea 2 Varianta centralizata | Personal exploatare-intretinere Statie de epurare | Personal exploatare-intretinere retele de canalizare
descarcare in | SEAU Sf Gheorghe existenta | 0 | 0
SEAU Sfantu Gheorghe
| TOTAL | 0 | 0
| TOTAL GENERAL | 0

## Cheltuieli energie
CHELTUIELI ENERGIE (Euro/an)
ƞ
Optiunea 1 |  |  | PENTRU SEAU, CONSUMUL DE ENERIGIE SE CALCULEAZA IN SHEET-Ul aferent SEAU | [7 empty] | Pcons= Q*H/102/ƞ | 0.6
Varianta descentralizata |  |  | EXEMPLU CALCUL CONSUM ENERIE pentru SPAU | [8 empty] | 102
| Putere consumata (kW) | Consum energie (kwH/an) | SPAU | Q pompa |  | H pomp | Putere consumata | Qzi med | Qor max | Q an med | Nr ore functionare Pompe | Consum anunal
SEAU Sanzieni noua | 58.134 | 230967.9174 |  | l/s | mc/zi | mCA | kwh | l/s | l/s | mc/an | ore/zi | kwh/an
|  |  | SPAU 1 | 13.4 | 1157.76 | 53 | 11.6046 | 4.99 | 13.4 | 1821.35 | 8.9373 | 37855.5098
|  |  | SPAU 2 | 0 | 0 | 0 | 0 | 4.99 | 0 | 1821.35 | #DIV/0! | #DIV/0!
[5 empty] | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
TOTAL | 58.134 | 230967.9174 |  |  | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
[5 empty] | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
[5 empty] | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
Optiunea 2 |  |  |  |  | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
Varianta centralizata |  |  |  |  | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
| Putere consumata (kW) | Consum energie (kwH/an) |  |  | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
[5 empty] | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
Statie de pompare apa uzata | 11.6046 | 37855.5098 |  |  | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
SEAU Targu Secuiesc pentru Sanzieni | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | #DIV/0! | #DIV/0!
48.2667
TOTAL | 11.6046 | 37855.5098
Note on K6: Maria Popescu: din breviar:Qzi med+Qinfiltratii
Note on D12: Maria Popescu: La aceasta valoare se face link in sheet-ul "analiza optiuni" (C71, D71 …)

## Cheltuieli materiale
Materiale | Optiunea 1 | Optiunea 2
Chimicale | 3893.0679 | 3893.0679
Consumabile | 0 | 0
TOTAL | 3893.0679 | 3893.0679

## Desfacere-refacere
DESFACERE SI REFACERE DRUM RUTIER,
LUNGIME CONDUCTA, L=1m
TIP | Diametre conducte De | LUCRARI INCLUSE | LATIME SANT | DENUMIRE STRAT DE BAZA | PRET UNITAR | TOTAL (fara profit) | TOTAL CU COEFICIENT SF 15% (fara profit).
| mm |  | m |  | EURO/MP | EURO/ML | EURO/ML
1A | 50 - 100 | 1. Desfacere. 2. Refacere:fundatie 20cm, binder 6cm, ASFALT 3cm. | 0.7 | ASFALT | 79 | 55.3 | 63.595
1B |  | 1. Desfacere. 2. Refacere:strat balast 20cm, BETON 20cm | 0.7 | BETON | 78.03 | 54.621 | 62.8141
1C |  | 1. Desfacere. 2. Refacere:strat balast 20cm, MACADAM 20cm | 0.7 | MACADAM | 16.75 | 11.725 | 13.4837
2A | 100 - 200 | 1. Desfacere. 2. Refacere:fundatie 20cm, binder 6cm, ASFALT 3cm. | 0.8 | ASFALT | 79 | 63.2 | 72.68
2B |  | 1. Desfacere. 2. Refacere:strat balast 20cm, BETON 20cm | 0.8 | BETON | 78.03 | 62.424 | 71.7876
2C |  | 1. Desfacere. 2. Refacere:strat balast 20cm, MACADAM 20cm | 0.8 | MACADAM | 16.75 | 13.4 | 15.41
3A | 200 - 300 | 1. Desfacere. 2. Refacere:fundatie 20cm, binder 6cm, ASFALT 3cm. | 0.9 | ASFALT | 79 | 71.1 | 81.765
3B |  | 1. Desfacere. 2. Refacere:strat balast 20cm, BETON 20cm | 0.9 | BETON | 78.2 | 70.38 | 80.937
3C |  | 1. Desfacere. 2. Refacere:strat balast 20cm, MACADAM 20cm | 0.9 | MACADAM | 16.75 | 15.075 | 17.3362
4A | 300 - 400 | 1. Desfacere. 2. Refacere:fundatie 20cm, binder 6cm, ASFALT 3cm. | 1 | ASFALT | 79 | 79 | 90.85
4B |  | 1. Desfacere. 2. Refacere:strat balast 20cm, BETON 20cm | 1 | BETON | 78.2 | 78.2 | 89.93
4C |  | 1. Desfacere. 2. Refacere:strat balast 20cm, MACADAM 20cm | 1 | MACADAM | 16.75 | 16.75 | 19.2625
5A | 400 - 600 | 1. Desfacere. 2. Refacere:fundatie 20cm, binder 6cm, ASFALT 3cm. | 1.15 | ASFALT | 79.2 | 91.08 | 104.742
5B |  | 1. Desfacere. 2. Refacere:strat balast 20cm, BETON 20cm | 1.15 | BETON | 78.24 | 89.976 | 103.4724
5C |  | 1. Desfacere. 2. Refacere:strat balast 20cm, MACADAM 20cm | 1.15 | MACADAM | 16.75 | 19.2625 | 22.1519
6A | 600 - 800 | 1. Desfacere. 2. Refacere:fundatie 20cm, binder 6cm, ASFALT 3cm. | 1.35 | ASFALT | 79.2 | 106.92 | 122.958
6B |  | 1. Desfacere. 2. Refacere:strat balast 20cm, BETON 20cm | 1.35 | BETON | 78.24 | 105.624 | 121.4676
6C |  | 1. Desfacere. 2. Refacere:strat balast 20cm, MACADAM 20cm | 1.35 | MACADAM | 16.75 | 22.6125 | 26.0044

## SEAU_Belin
DESFASURATOR SUB-OBIECTE
STATIE DE EPURARE BELIN 2.700 l.e. - Tehnologia SBR
Cost unitar
Nr crt | DENUMIREA OBIECTELOR | TOTAL | C + I | MU | U
|  |  | (EUR) | (EUR) | (EUR)
0 | 1 | 2 | 3 | 4 | 5
Statia de epurare Belin
1 | Gratare rare | 74270 | 40500 | 3070 | 30700 | Pavilion tehnologic |  | 300 | / m2
2 | Statie pompare influent | 18301.4 | 1500 | 1527.4 | 15274 |  |  | 250 | / m3 util
3 | Gratare dese-deznisipator/separator grasimi | 68983.2 | 0 | 6271.2 | 62712 | C+I inclus la "Gratare rare"
4 | Bazin uniformizare debite si incarcari | 33726.4 | 14175 | 1777.4 | 17774 |  |  | 175 | / m3 util
5 | Reactoare biologice | 253681 | 159950 | 8521 | 85210 |  |  | 175 | / m3 util
6 | Statie de suflante | 26439 | 7200 | 1749 | 17490 |  |  | 300 | / m2
7 | Tratare chimica | 7150 | 0 | 650 | 6500 | C+I inclus la "Gratare rare"
8 | Dezinfectie cu UV | 6750 | 1250 | 500 | 5000 | estimare |  | 250 | / m3 util
9 | Ingrosator gravitational namol in exces | 45942.1 | 6000 | 3631.1 | 36311 |  |  | 250 | / m3 util
10 | Deshidratare mecanica | 78059 | 30000 | 4369 | 43690 |  |  | 300 | / m2
11 | Preparare si dozare polimeri | 7095 | 0 | 645 | 6450 | C+I inclus la "Deshidratare mecanica"
12 | Statie pompare supernatant | 7027.2 | 1250 | 525.2 | 5252 |  |  | 250 | / m3 util
13 | Statie pompare apa tehnologica | 11140 | 8500 | 240 | 2400 |  |  | 250 | / m3 util
14 | Statie de pompare ape meteorice | 8957 | 2500 | 587 | 5870 |  |  | 250 | / m3 util
15 | Statie pompare apa potabila + rezerva de incendiu | 14000 | 8500 | 500 | 5000 | de modificat cf Aviz ISU!!!! |  | 250 | / m3 util
16 | Platforme depozitare namol | 0 | 0 | 0 | 0 |  |  | 300 | / m2
17 | Conducta descarcare efluent | 10800 | 10800 | 0 | 0 | lungime 200m
18 | Gura de descarcare | 10000 | 10000 | 0 | 0
19 | Cladire administrativa | 11000 | 11000 | 0 | 0 | container |  | 250 | / m2
20 | Echipamente electrice de proces | 110000 | 0 | 10000 | 100000
21 | HVAC | 7700 | 0 | 700 | 7000
22 | Conducte tehnologice exterioare | 35000 | 35000 | 0 | 0 |  |  | 7 | euro / l.e.
23 | Conducte interioare si accesorii | 27500 | 0 | 2500 | 25000 |  |  | 5 | euro / l.e.
24 | Instalatii de automatizare si control (SCADA) | 30000 | 0 | 0 | 30000
25 | Bransament electric + PT | 80000 | 0 | 0 | 80000
26 | Lucrari amenajare SEAU (demolari, iluminat exterior, instalatii legare la paratrasnet, drumuri, zona parcare, garduri, porti) | 83575 | 83575 | 0 | 0
27 | Fundatii speciale - amenajare teren | 0 | 0 | 0 | 0
28 | Dotari cu echipamente de laborator | 0 | 0 | 0 | 0
29 | Active necorporate (licente SCADA) | 0 | 0 | 0 | 0 | 14.000 euro!!!
| TOTAL OBIECT | 1067096.3 | 431700 | 47763.3 | 587633 |  | 1067096.3 | verificare!!!!
| cost unitar SEAU | 395.2209 | / l.e.
|  | 2700 | l.e.
|  |  | Calcul lucrari amenajare SEAU |  | Cost total - euro
|  |  | Instalatii electrice exterioare |  | 43000
|  |  | Drumuri in incinta, platforme, parcari |  | 30000
|  |  | Imprejmuire, porti acces |  | 10575
|  |  | Cost total |  | 83575

## EE_Belin
SEAU Belin | 2700 | l.e.
Echipament | Instalat | Unităţi de serviciu | Putere instalată (cotaţie) (kW/unitate) | Putere instalată (kW/totala) | Putere absorbită (kW / unitate) | Putere absorbita (kW/totala) | Timp de funcţionare zilnică (h/zi) | Necesarul zilnic de curent electric (kWh/zi) | Timp de funcţionare (zile / an) | Consum de energie (kWh / an)
Gratare rare
Gratar rar | 1 | 1 | 0.25 | 0.25 | 0.2 | 0.2 | 4 | 0.8 | 365 | 292
Transportor/compactor retineri gratare rare | 1 | 1 | 1.5 | 1.5 | 1.2 | 1.2 | 5.6 | 6.72 | 365 | 2452.8 | 2744.8
Statie de pompare influent
Pompe de ridicare | 3 | 2 | 3.5 | 10.5 | 2.35 | 4.7 | 10.7309 | 50.4351 | 365 | 18408.8099
Mixer amestec | 1 | 1 | 1.5 | 1.5 | 1.2 | 1.2 | 13.2691 | 15.923 | 365 | 5811.8783
Unitati mecanice compacte
Gratar des | 2 | 2 | 0.55 | 1.1 | 0.44 | 0.88 | 4 | 3.52 | 365 | 1284.8
Transportor/Compactor retineri gratare dese | 2 | 2 | 0.25 | 0.5 | 0.2 | 0.4 | 5.2 | 2.08 | 365 | 759.2
Transportor nisip | 2 | 2 | 0.37 | 0.74 | 0.296 | 0.592 | 5.2 | 3.0784 | 365 | 1123.616 |  | Qu zi med | = | 337.88 | m3/zi
Clasificator nisip | 2 | 2 | 0.25 | 0.5 | 0.2 | 0.4 | 5.2 | 2.08 | 365 | 759.2 |  | Qu zi max | = | 403.91 | m3/zi
Compresor | 2 | 2 | 0.25 | 0.5 | 0.2 | 0.4 | 24 | 9.6 | 365 | 3504 |  | Qu or max | = | 37.64 | m3/h
Pompa grasimi | 2 | 2 | 0.18 | 0.36 | 0.144 | 0.288 | 2 | 0.576 | 365 | 210.24 | 7641.056
Bazin de uniformizare debite si pompare apa pretratata
Pompe apa pretratata | 3 | 2 | 3.5 | 10.5 | 2.35 | 4.7 | 10.4 | 48.88 | 365 | 17841.2
Mixer amestec | 1 | 1 | 2.75 | 2.75 | 1.95 | 1.95 | 13.6 | 26.52 | 365 | 9679.8
Reactoare biologice - SBR. Suflante reactoare biologice
Mixer amestec | 2 | 2 | 2.1 | 4.2 | 1.4 | 2.8 | 13.6 | 38.08 | 365 | 13899.2
Decanter | 2 | 2 | 1.5 | 3 | 1.2 | 2.4 | 10.4 | 24.96 | 365 | 9110.4
Suflante reactoare biologice | 3 | 2 | 5.5 | 16.5 | 4.29 | 8.58 | 12.8 | 109.824 | 365 | 40085.76
Dezinfectie cu UV
Lampi UV | 2 | 2 | 4 | 8 | 3.2 | 6.4 | 24 | 153.6 | 365 | 56064
Stocare si dozare reactiv precipitare fosfor
Pompe dozare FeCl3 | 2 | 1 | 0.37 | 0.74 | 0.296 | 0.296 | 2.4 | 0.7104 | 365 | 259.296
Pompe transfer FeCl3 | 1 | 1 | 0.65 | 0.65 | 0.52 | 0.52 | 0.5 | 0.26 | 12 | 3.12
Rezistenta electrica | 1 | 1 | 4.5 | 4.5 | 4.5 | 4.5 | 24 | 108 | 90 | 9720
Statie pompare efluent
Pompe de ridicare | 3 | 2 | 3.5 | 10.5 | 2.8 | 5.6 | 10.7309 | 60.0929 | 365 | 21933.9012
Ingrosator gravitational namol in exces
Pompe extractie namol in exces | 2 | 1 | 0.37 | 0.74 | 0.296 | 0.296 | 2.4 | 0.7104 | 365 | 259.296
Pod raclor cu hersa | 1 | 1 | 0.12 | 0.12 | 0.096 | 0.096 | 24 | 2.304 | 365 | 840.96 | 2414.256
Pompe namol ingrosat | 2 | 1 | 0.75 | 1.5 | 0.6 | 0.6 | 6 | 3.6 | 365 | 1314
Deshidratare mecanica namol
Instalatie de conditionare - mixer | 1 | 1 | 0.55 | 0.55 | 0.44 | 0.44 | 6 | 2.64 | 365 | 963.6
Pompe alimentare | 2 | 1 | 0.75 | 1.5 | 0.6 | 0.6 | 6 | 3.6 | 365 | 1314
Centrifuga (tambur si surub) | 1 | 1 | 4 | 4 | 3.2 | 3.2 | 6 | 19.2 | 365 | 7008
Transportor namol deshidratat | 1 | 1 | 0.25 | 0.25 | 0.2 | 0.2 | 6 | 1.2 | 365 | 438 | 9723.6
Unitate de preparare si dozare polimer
Unitate preparare si dozare polimeri | 1 | 1 | 0.55 | 0.55 | 0.44 | 0.44 | 6 | 2.64 | 365 | 963.6
Pompe dozare deshidratare | 2 | 1 | 0.37 | 0.74 | 0.296 | 0.296 | 6 | 1.776 | 365 | 648.24 | 1611.84
Statie pompare supernatant
Pompe supernatant | 2 | 1 | 1.1 | 2.2 | 1.1 | 1.1 | 4 | 4.4 | 365 | 1606
Statie pompare apa potabila
Statie pompare apa potabila | 2 | 1 | 1.1 | 2.2 | 1.1 | 1.1 | 6 | 6.6 | 365 | 2409
Grup pompare apa tehnologica
Grup pompare apa tehnologica | 1 | 1 | 1.1 | 1.1 | 0.88 | 0.88 | functionare ocazionala
Statie de pompare apa meteorica
Statie de pompare apa meteorica | 1 | 1 | 1.1 | 1.1 | 0.88 | 0.88 | functionare ocazionala
|  |  |  | 95.34 |  | 58.134 |  |  | TOTAL | 230967.9174

## Echip.tehn_Belin
Proiect: | SEAU Belin
| COST ECHIPAMENTE TEHNOLOGICE |  |  |  |  | 1euro=
Cod | Echipament | Instalat | Unitati in serviciu | Lista date tehnice/Spec | Cost unitar (euro) | Cost total (euro)
Obiect tehnologic
| Gratare rare | [5 empty] | 30700
| Gratar rar automat | 1 |  |  | 12000 | 12000
| Vana de perete amonte/aval | 2 |  |  | 2000 | 4000
| Transportor/compactor retineri gratare rare https://www.huber.de/products/screens-and-fine-screens/step-screenrs/huber-fine-screen-step-screenr-ssv.html | 1 |  |  | 3500 | 3500
| Containere 1m3 | 2 |  |  | 600 | 1200
| Echipament dezodorizare | 1 |  |  | 10000 | 10000 |  | Air filter for odor removal by catalytic activated carbon - MEVA
| Statie de pompare influent | [5 empty] | 15274
| Pompe de ridicare | 3 |  |  | 3858 | 11574
| Mixer | 1 |  |  | 1500 | 1500
| Echipament de ridicare | 1 |  |  | 2200 | 2200
| Unitati mecanice compacte | [5 empty] | 62712
| Unitati compacte deznisiptor-separator de grasimi | 2 |  |  | 26535 | 56862
| Containere 1,1m3 (4 buc) si 0,5 m3 (4 buc) | 8 |  |  | 600 | 4800
| Ventilator axial | 1 |  |  | 1050 | 1050
| Bazin de uniformizare debite si pompare apa pretratata | [5 empty] | 17774
| Pompe apa pretratata | 3 |  |  | 3858 | 11574
| Monorai cu palan | 1 |  |  | 700 | 700
| Mixer amestec | 1 |  |  | 5500 | 5500
| Reactoare biologice - SBR. Suflante reactoare biologice | [5 empty] | 85210
| Mixer | 2 |  |  | 10000 | 20000
| Decanter | 2 |  |  | 26200 | 52400
| Sistem aerare | 2 |  |  | 5715 | 11430
| Pompa mobila golire bazine SBR | 1 |  |  | 1380 | 1380
| Tratare chimica - reactiv precipitare fosfor | [5 empty] | 6500
| Rezervor stocare clorura ferica - 1m3 | 1 |  |  | 2000 | 2000
| Pompe de dozare clorura ferica | 2 |  |  | 1500 | 3000
| Cabinet de transfer | 1 |  |  | 1500 | 1500
| Dezinfectie cu UV | [5 empty] | 5000
| Echipament dezinfectie in-line | 1 |  |  | 5000 | 5000
| Cladire suflante | [5 empty] | 17490
| Suflante reactoare biologice | 3 |  |  | 5130 | 15390
| Monorail cu palan pt suflante | 3 |  |  | 700 | 2100
| Ingrosator gravitational namol in exces | [5 empty] | 36311
| Pompe extractie namol in exces | 2 |  |  | 2800 | 5600
| Monorai cu palan | 1 |  |  | 700 | 700
| Pod raclor cu hersa | 1 |  |  | 11735 | 13811
| Deversor metalic reglabil (AISI316L) | 1 |  |  | 8200 | 8200
| Pompe namol ingrosat | 2 |  |  | 4000 | 8000
| Deshidratare mecanica namol | [5 empty] | 43690
| Mixer in-line | 1 |  |  | 1260 | 1260
| Reactor amestec | 1 |  |  | 3600 | 3600
| Pompe alimentare | 2 |  |  | 4000 | 8000
| Echipament deshidratare - centrifuga | 1 |  |  | 21380 | 21380
| Transportor namol deshidratat | 1 |  |  | 4700 | 4700
| Containere | 2 |  |  | 1000 | 2000
| Monorail cu palan | 1 |  |  | 700 | 700
| Ventilator axial | 1 |  |  | 1050 | 1050
| Dus de securitate | 1 |  |  | 1000 | 1000
| Unitate de preparare si dozare polimer | [5 empty] | 6450
| Unitate preparare si dozare polimeri | 1 |  |  | 4450 | 4450
| Pompe dozare polimer | 2 |  |  | 1000 | 2000
| Statie pompare supernatant | [5 empty] | 5252
| Statie pompare supernatant | 2 |  |  | 1876 | 3752
| Suport macara mobila | 1 |  |  | 1500 | 1500
| Statie pompare apa tehnologica | [5 empty] | 2400
| Grup booster apa epurata | 1 |  |  | 2300 | 2300
| Recipient hidrofor cu membrana sub presiune + pompa de basa | 1 |  |  | 100 | 100
| Pre-epurare ape meteorice | [5 empty] | 5870
| Instalatie pre-epurare ape meteorice | 1 |  |  | 870 | 870 |  | volum retentie 10m3
| Statie de pompare ape meteorice | 2 |  |  | 2500 | 5000
| Grup de pompare apa potabila | [5 empty] | 5000
| Grup de pompare si hidrofor cu membrana | 1 |  |  | 5000 | 5000
| Statie receptie vidanja | [5 empty] | 0
| Statie receptie vidanja | 1 |  |  | 0 | 0
|  |  |  | Total utilaje de proces = |  | 345633
0

## Reactivi_Belin
SEAU Belin | 2700 | l.e. |  |  |  | euro | 4.7517
Eliminare fosfor | [5 empty] | Costuri reactivi
Necesar clorura ferica |  |  | kg/zi | 17.6 | cf Breviar de calcul | Polimeri |  | 16060 | lei/tona | 3379.843 | euro/tona
|  |  | l/zi | 12.3944 |  | Clorura ferica 40% |  | 1460 | lei/tona | 307.2585 | euro/tona
Consum anual de clorura ferica |  |  | to/an | 6.424
Tratarea namolului: | [5 empty] | COST TOTAL REACTIVI |  |  |  | 3893.0679 | euro/an
Productie de namol: |  |  | kgSU / zi | 158.75 | cf Breviar de calcul
Cantitate namol ingrosat |  |  | kgSU/zi | 155.575 | cf Breviar de calcul
Captura namol deshidratare |  |  | % | 98
Cantitate namol deshidratat |  |  | kgSU/zi | 153.9881 | inclusiv PE
Cantitate de namol deshidratat |  |  | kg/zi | 615.9525
Cantitate anuala de namol deshidratat |  |  | to/an | 224.8227
Procent SU in namolul deshidratat |  |  | % | 22
Greutatea specifica a namolului deshidratat |  |  | kg/m3 | 1080
Masa de substanta uscata pe unitatea de volum |  |  | kg/m3 | 237.6
Volum zilnic de namol deshidratat |  |  | m3/zi | 0.6481
Volum anual de namol rezultat |  |  | m3/an | 236.5558
Consum specific de polielectrolit |  |  | gPE/kgSU | 10 | cf Breviar de calcul
Consum zilnic maxim polielectrolit |  |  | kgPE/zi | 1.5557
Consum anual maxim polielectrolit |  |  | toPE/an | 0.56785
Concentratia solutiei primare de polielectrolit |  |  | % | 0.5
Densitatea solutiei primare de polielectrolit |  |  | kg/m3 | 1000
Consumul de solutie primara de polielectrolit |  |  | m3/zi | 0.31115 | cf Breviar de calcul
Concentratia solutiei de polielectrolit diluata |  |  | % | 0.1
Consumul de apa de dilutie |  |  | m3/zi | 1.2446 | cf Breviar de calcul
Consum anual apa de dilutie |  |  | m3/an | 454.279